## DGA
DGA evaluation
Samples
|  | Date | 2015-09-03 09:00 | 2014-01-14 | 2012-06-26 | 2010-12-02 | 2010-07-08 | 2009-10-09 | 2009-02-25 | 2008-09-04 | 2008-03-14 | 2007-11-08 | 2007-04-19 | 2006-11-30 | 2006-01-31 | 2005-07-13 | 2005-02-10 | 2004-08-26 | 2004-02-05 | 2003-07-17 | 2003-01-15 | 2002-08-12 | 2002-01-18 | 2001-08-07 | 2001-02-16 | 2000-10-09 | 2000-02-11 | 1999-07-23 | 1999-02-11 | 1997-12-22 | 1997-06-25 | 1997-01-02 | 1996-07-01 | 1993-10-25
[ppm] | Hydrogen | H2 | 21 | 4 | 4.8 | 17.2 | 17.7 | 17.7 | 10.7 | 14.1 | 13.3 | 14.8 | 14.7 | 23.7 | 20.2 | 15.7 | 14.3 | 23.9 | 17 | 20.1 | 17.3 | 5.4 | 2.9 | 13.3 | 8.8 | 7.8 | 7.4 | 11 | 16.9 | 19 | 7 | 15 | 8 | 19
[ppm] | Carbon monoxide | CO | 305 | 52.7 | 284.9 | 373.3 | 365.7 | 384.7 | 350.1 | 369.3 | 347.8 | 368.5 | 368.7 | 460 | 480.6 | 390.1 | 467.4 | 528.3 | 447.9 | 438.9 | 376.6 | 219.8 | 182.9 | 335.2 | 272.6 | 206 | 288 | 382 | 382 | 331 | 225 | 345 | 335 | 193
[ppm] | Carbon dioxide | CO2 | 3.8 | 1.45 | 4.49 | 5.61 | 6.25 | 6.44 | 6.46 | 6.89 | 6.64 | 7.41 | 7.97 | 9.05 | 11.23 | 7.59 | 11.31 | 12.93 | 8.67 | 7.06 | 7.36 | 5.96 | 4.8 | 8.8 | 5.95 | 5.02 | 6.71 | 7.62 | 6.67 | 6 | 5 | 4.4 | 5 | 5
[ppm] | Methane | CH4 | 3 | 1.4 | 3.6 | 5 | 4.9 | 4.9 | 4.9 | 4.8 | 4.4 | 4.7 | 5.2 | 6.3 | 6.8 | 6.4 | 6.7 | 6.9 | 5.3 | 5.9 | 5.8 | 3.6 | 3.8 | 5.5 | 4.7 | 3.7 | 6.1 | 7 | 7.2 | 7 | 7 | 7 | 7 | 3
[ppm] | Ethene | C2H4 | 0.09 | 2.8 | 6.8 | 6.5 | 5.3 | 3.6 | 2.7 | 2.2 | 1.6 | 1.9 | 2.6 | 2.6 | 3 | 0 | 0 | 2.3 | 0 | 0 | 0 | 0 | 2.1 | 3.4 | 2.3 | 1.9 | 3.6 | 2.8 | 3.3 | 3 | 3 | 3 | 3 | 1
[ppm] | Ethane | C2H6 | 1 | 0.9 | 4 | 4.5 | 4.5 | 4.4 | 4.6 | 4.7 | 4.5 | 4.6 | 5.8 | 7.2 | 9.2 | 7.6 | 10.4 | 10.4 | 7.7 | 10 | 10.6 | 6.9 | 7 | 11 | 8.6 | 7 | 10 | 11 | 9.6 | 9 | 8 | 7 | 6 | 4
[ppm] | Ethyne (Acetylene) | C2H2 | 0.09 | 0.6 | 2.8 | 4.5 | 5.4 | 5.5 | 5.1 | 5.1 | 4.4 | 4.5 | 4.7 | 4.7 | 3.3 | 2.1 | 2.4 | 2 | 1.6 | 0 | 1.3 | 1.4 | 0.1 | 1.2 | 0.9 | 0.7 | 2 | 1.4 | 1.1 | 2 | 2 | 1 | 1 | 0

## DGAF
Scoring criteria |  | Weighting | Gas scores | Weighted scores | DGAF |  | Scoring criteria |  | Weighting | Gas scores | Weighted scores | DGAF
Hydrogen | H2 | 2 | 1 | 2 | 1 | 1993-10-25 | Hydrogen | H2 | 2 | 1 | 2 | 1.1667 | 2010-07-08 |  | 1 | 2 | 3 | 4 | 5 | 6 | Wi
Carbon monoxide | CO | 1 | 1 | 1 |  |  | Carbon monoxide | CO | 1 | 4 | 4 |  |  | H2 | 100 | 200 | 300 | 500 | 700 | >700 | 2
Carbon dioxide | CO2 | 1 | 1 | 1 |  |  | Carbon dioxide | CO2 | 1 | 1 | 1 |  |  | CO | 350 | 700 | 900 | 1100 | 1400 | >1400 | 1
Methane | CH4 | 3 | 1 | 3 |  |  | Methane | CH4 | 3 | 1 | 3 |  |  | CO2 | 2500 | 3000 | 4000 | 5000 | 7000 | >7000 | 1
Ethene | C2H4 | 3 | 1 | 3 |  |  | Ethene | C2H4 | 3 | 1 | 3 |  |  | CH4 | 75 | 125 | 200 | 400 | 600 | >600 | 3
Ethane | C2H6 | 3 | 1 | 3 |  |  | Ethane | C2H6 | 3 | 1 | 3 |  |  | C2H4 | 50 | 80 | 100 | 150 | 200 | >200 | 3
Ethyne (Acetylene) | C2H2 | 5 | 1 | 5 |  |  | Ethyne (Acetylene) | C2H2 | 5 | 1 | 5 |  |  | C2H6 | 65 | 80 | 100 | 120 | 150 | >150 | 3
[14 empty] | C2H2 | 3 | 7 | 35 | 50 | 80 | >80 | 5
Rating | Number | [5 empty] | Rating | Number
A | 4 | [5 empty] | A | 4 | [9 empty] | Rating Code
[18 empty] | A | 1.2 | Good
[18 empty] | B | 1.5 | Acceptable
[18 empty] | C | 2 | Need Caution
[18 empty] | D | 3 | Poor
Scoring criteria |  | Weighting | Gas scores | Weighted scores | DGAF |  | Scoring criteria |  | Weighting | Gas scores | Weighted scores | DGAF | [5 empty] | E | >=3 | Very Poor
Hydrogen | H2 | 2 | 1 | 2 | 1 | 1996-07-01 | Hydrogen | H2 | 2 | 1 | 2 | 1.3333 | 2010-12-02
Carbon monoxide | CO | 1 | 1 | 1 |  |  | Carbon monoxide | CO | 1 | 2 | 2 | [6 empty] | Rating Code
Carbon dioxide | CO2 | 1 | 1 | 1 |  |  | Carbon dioxide | CO2 | 1 | 1 | 1 | [6 empty] | A
Methane | CH4 | 3 | 1 | 3 |  |  | Methane | CH4 | 3 | 1 | 3 | [6 empty] | B
Ethene | C2H4 | 3 | 1 | 3 |  |  | Ethene | C2H4 | 3 | 1 | 3 | [6 empty] | C
Ethane | C2H6 | 3 | 1 | 3 |  |  | Ethane | C2H6 | 3 | 1 | 3 | [6 empty] | D
Ethyne (Acetylene) | C2H2 | 5 | 1 | 5 |  |  | Ethyne (Acetylene) | C2H2 | 5 | 2 | 10 | [6 empty] | E
Rating | Number | [5 empty] | Rating | Number | [9 empty] | Rating Code
A | 4 | [5 empty] | B | 3 | [9 empty] | A
B
C
D
E
Scoring criteria |  | Weighting | Gas scores | Weighted scores | DGAF |  | Scoring criteria |  | Weighting | Gas scores | Weighted scores | DGAF
Hydrogen | H2 | 2 | 1 | 2 | 1 | 1997-01-02 | Hydrogen | H2 | 2 | 1 | 2 | 1 | 2012-06-26 |  |  |  |  | Rating Code
Carbon monoxide | CO | 1 | 1 | 1 |  |  | Carbon monoxide | CO | 1 | 1 | 1 | [6 empty] | A
Carbon dioxide | CO2 | 1 | 1 | 1 |  |  | Carbon dioxide | CO2 | 1 | 1 | 1 | [6 empty] | B
Methane | CH4 | 3 | 1 | 3 |  |  | Methane | CH4 | 3 | 1 | 3 | [6 empty] | C
Ethene | C2H4 | 3 | 1 | 3 |  |  | Ethene | C2H4 | 3 | 1 | 3 | [6 empty] | D
Ethane | C2H6 | 3 | 1 | 3 |  |  | Ethane | C2H6 | 3 | 1 | 3 | [6 empty] | E
Ethyne (Acetylene) | C2H2 | 5 | 1 | 5 |  |  | Ethyne (Acetylene) | C2H2 | 5 | 1 | 5
Rating Code
Rating | Number | [5 empty] | Rating | Number | [9 empty] | A
A | 4 | [5 empty] | A | 4 | [9 empty] | B
C
D
E
Scoring criteria |  | Weighting | Gas scores | Weighted scores | DGAF |  | Scoring criteria |  | Weighting | Gas scores | Weighted scores | DGAF | [5 empty] | Rating Code
Hydrogen | H2 | 2 | 1 | 2 | 1 | 1997-06-25 | Hydrogen | H2 | 2 | 1 | 2 | 1 | 2014-01-14 |  |  |  |  | A
Carbon monoxide | CO | 1 | 1 | 1 |  |  | Carbon monoxide | CO | 1 | 1 | 1 | [6 empty] | B
Carbon dioxide | CO2 | 1 | 1 | 1 |  |  | Carbon dioxide | CO2 | 1 | 1 | 1 | [6 empty] | C
Methane | CH4 | 3 | 1 | 3 |  |  | Methane | CH4 | 3 | 1 | 3 | [6 empty] | D
Ethene | C2H4 | 3 | 1 | 3 |  |  | Ethene | C2H4 | 3 | 1 | 3 | [6 empty] | E
Ethane | C2H6 | 3 | 1 | 3 |  |  | Ethane | C2H6 | 3 | 1 | 3
Ethyne (Acetylene) | C2H2 | 5 | 1 | 5 |  |  | Ethyne (Acetylene) | C2H2 | 5 | 1 | 5 | [6 empty] | Rating Code
A
Rating | Number | [5 empty] | Rating | Number | [9 empty] | B
A | 4 | [5 empty] | A | 4 | [9 empty] | C
D
E
[23 empty] | 1 | 2 | 3 | 4 | 5 | 6 | Wi
Scoring criteria |  | Weighting | Gas scores | Weighted scores | DGAF |  | Scoring criteria |  | Weighting | Gas scores | Weighted scores | DGAF | [9 empty] | H2 | 100 | 200 | 300 | 500 | 700 | >700 | 2
Hydrogen | H2 | 2 | 1 | 2 | 1 | 1997-12-22 | Hydrogen | H2 | 2 | 1 | 2 | 1 | 2015-09-03 09:00 | [8 empty] | CO | 350 | 700 | 900 | 1100 | 1400 | >1400 | 1
Carbon monoxide | CO | 1 | 1 | 1 |  |  | Carbon monoxide | CO | 1 | 1 | 1 | [10 empty] | CO2 | 2500 | 3000 | 4000 | 5000 | 7000 | >7000 | 1
Carbon dioxide | CO2 | 1 | 1 | 1 |  |  | Carbon dioxide | CO2 | 1 | 1 | 1 | [10 empty] | CH4 | 75 | 125 | 200 | 400 | 600 | >600 | 3
Methane | CH4 | 3 | 1 | 3 |  |  | Methane | CH4 | 3 | 1 | 3 | [10 empty] | C2H4 | 50 | 80 | 100 | 150 | 200 | >200 | 3
Ethene | C2H4 | 3 | 1 | 3 |  |  | Ethene | C2H4 | 3 | 1 | 3 | [10 empty] | C2H6 | 65 | 80 | 100 | 120 | 150 | >150 | 3
Ethane | C2H6 | 3 | 1 | 3 |  |  | Ethane | C2H6 | 3 | 1 | 3 | [10 empty] | C2H2 | 3 | 7 | 35 | 50 | 80 | >80 | 5
Ethyne (Acetylene) | C2H2 | 5 | 1 | 5 |  |  | Ethyne (Acetylene) | C2H2 | 5 | 1 | 5
Rating | Number | [5 empty] | Rating | Number
A | 4 | [5 empty] | A | 4
Scoring criteria |  | Weighting | Gas scores | Weighted scores | DGAF
Hydrogen | H2 | 2 | 1 | 2 | 1.0556 | 1999-02-11
Carbon monoxide | CO | 1 | 2 | 2
Carbon dioxide | CO2 | 1 | 1 | 1
Methane | CH4 | 3 | 1 | 3
Ethene | C2H4 | 3 | 1 | 3
Ethane | C2H6 | 3 | 1 | 3
Ethyne (Acetylene) | C2H2 | 5 | 1 | 5
Rating | Number
A | 4
Scoring criteria |  | Weighting | Gas scores | Weighted scores | DGAF
Hydrogen | H2 | 2 | 1 | 2 | 1.0556 | 1999-07-23
Carbon monoxide | CO | 1 | 2 | 2
Carbon dioxide | CO2 | 1 | 1 | 1
Methane | CH4 | 3 | 1 | 3
Ethene | C2H4 | 3 | 1 | 3
Ethane | C2H6 | 3 | 1 | 3
Ethyne (Acetylene) | C2H2 | 5 | 1 | 5
Rating | Number
A | 4
Scoring criteria |  | Weighting | Gas scores | Weighted scores | DGAF
Hydrogen | H2 | 2 | 1 | 2 | 1.1111 | 2000-02-11
Carbon monoxide | CO | 1 | 3 | 3
Carbon dioxide | CO2 | 1 | 1 | 1
Methane | CH4 | 3 | 1 | 3
Ethene | C2H4 | 3 | 1 | 3
Ethane | C2H6 | 3 | 1 | 3
Ethyne (Acetylene) | C2H2 | 5 | 1 | 5
Rating | Number
A | 4
Scoring criteria |  | Weighting | Gas scores | Weighted scores | DGAF
Hydrogen | H2 | 2 | 1 | 2 | 1 | 2000-10-09
Carbon monoxide | CO | 1 | 1 | 1
Carbon dioxide | CO2 | 1 | 1 | 1
Methane | CH4 | 3 | 1 | 3
Ethene | C2H4 | 3 | 1 | 3
Ethane | C2H6 | 3 | 1 | 3
Ethyne (Acetylene) | C2H2 | 5 | 1 | 5
Rating | Number
A | 4
Scoring criteria |  | Weighting | Gas scores | Weighted scores | DGAF
Hydrogen | H2 | 2 | 1 | 2 | 1 | 2001-02-16
Carbon monoxide | CO | 1 | 1 | 1
Carbon dioxide | CO2 | 1 | 1 | 1
Methane | CH4 | 3 | 1 | 3
Ethene | C2H4 | 3 | 1 | 3
Ethane | C2H6 | 3 | 1 | 3
Ethyne (Acetylene) | C2H2 | 5 | 1 | 5
Rating | Number
A | 4
Scoring criteria |  | Weighting | Gas scores | Weighted scores | DGAF
Hydrogen | H2 | 2 | 1 | 2 | 1 | 2001-08-07
Carbon monoxide | CO | 1 | 1 | 1
Carbon dioxide | CO2 | 1 | 1 | 1
Methane | CH4 | 3 | 1 | 3
Ethene | C2H4 | 3 | 1 | 3
Ethane | C2H6 | 3 | 1 | 3
Ethyne (Acetylene) | C2H2 | 5 | 1 | 5
Rating | Number
A | 4
Scoring criteria |  | Weighting | Gas scores | Weighted scores | DGAF
Hydrogen | H2 | 2 | 1 | 2 | 1 | 2002-01-18
Carbon monoxide | CO | 1 | 1 | 1
Carbon dioxide | CO2 | 1 | 1 | 1
Methane | CH4 | 3 | 1 | 3
Ethene | C2H4 | 3 | 1 | 3
Ethane | C2H6 | 3 | 1 | 3
Ethyne (Acetylene) | C2H2 | 5 | 1 | 5
Rating | Number
A | 4
Scoring criteria |  | Weighting | Gas scores | Weighted scores | DGAF
Hydrogen | H2 | 2 | 1 | 2 | 1 | 2002-08-12
Carbon monoxide | CO | 1 | 1 | 1
Carbon dioxide | CO2 | 1 | 1 | 1
Methane | CH4 | 3 | 1 | 3
Ethene | C2H4 | 3 | 1 | 3
Ethane | C2H6 | 3 | 1 | 3
Ethyne (Acetylene) | C2H2 | 5 | 1 | 5
Rating | Number
A | 4
Scoring criteria |  | Weighting | Gas scores | Weighted scores | DGAF
Hydrogen | H2 | 2 | 1 | 2 | 1.0556 | 2003-01-15
Carbon monoxide | CO | 1 | 2 | 2
Carbon dioxide | CO2 | 1 | 1 | 1
Methane | CH4 | 3 | 1 | 3
Ethene | C2H4 | 3 | 1 | 3
Ethane | C2H6 | 3 | 1 | 3
Ethyne (Acetylene) | C2H2 | 5 | 1 | 5
Rating | Number
A | 4
Scoring criteria |  | Weighting | Gas scores | Weighted scores | DGAF
Hydrogen | H2 | 2 | 1 | 2 | 1.0556 | 2003-07-17
Carbon monoxide | CO | 1 | 2 | 2
Carbon dioxide | CO2 | 1 | 1 | 1
Methane | CH4 | 3 | 1 | 3
Ethene | C2H4 | 3 | 1 | 3
Ethane | C2H6 | 3 | 1 | 3
Ethyne (Acetylene) | C2H2 | 5 | 1 | 5
Rating | Number
A | 4
Scoring criteria |  | Weighting | Gas scores | Weighted scores | DGAF
Hydrogen | H2 | 2 | 1 | 2 | 1.0556 | 2004-02-05
Carbon monoxide | CO | 1 | 2 | 2
Carbon dioxide | CO2 | 1 | 1 | 1
Methane | CH4 | 3 | 1 | 3
Ethene | C2H4 | 3 | 1 | 3
Ethane | C2H6 | 3 | 1 | 3
Ethyne (Acetylene) | C2H2 | 5 | 1 | 5
Rating | Number
A | 4
Scoring criteria |  | Weighting | Gas scores | Weighted scores | DGAF
Hydrogen | H2 | 2 | 1 | 2 | 1.0556 | 2004-08-26
Carbon monoxide | CO | 1 | 2 | 2
Carbon dioxide | CO2 | 1 | 1 | 1
Methane | CH4 | 3 | 1 | 3
Ethene | C2H4 | 3 | 1 | 3
Ethane | C2H6 | 3 | 1 | 3
Ethyne (Acetylene) | C2H2 | 5 | 1 | 5
Rating | Number
A | 4
Scoring criteria |  | Weighting | Gas scores | Weighted scores | DGAF
Hydrogen | H2 | 2 | 1 | 2 | 1.0556 | 2005-02-10
Carbon monoxide | CO | 1 | 2 | 2
Carbon dioxide | CO2 | 1 | 1 | 1
Methane | CH4 | 3 | 1 | 3
Ethene | C2H4 | 3 | 1 | 3
Ethane | C2H6 | 3 | 1 | 3
Ethyne (Acetylene) | C2H2 | 5 | 1 | 5
Rating | Number
A | 4
Scoring criteria |  | Weighting | Gas scores | Weighted scores | DGAF
Hydrogen | H2 | 2 | 1 | 2 | 1.0556 | 2005-07-13
Carbon monoxide | CO | 1 | 2 | 2
Carbon dioxide | CO2 | 1 | 1 | 1
Methane | CH4 | 3 | 1 | 3
Ethene | C2H4 | 3 | 1 | 3
Ethane | C2H6 | 3 | 1 | 3
Ethyne (Acetylene) | C2H2 | 5 | 1 | 5
Rating | Number
A | 4
Scoring criteria |  | Weighting | Gas scores | Weighted scores | DGAF
Hydrogen | H2 | 2 | 1 | 2 | 1.3333 | 2006-01-31
Carbon monoxide | CO | 1 | 2 | 2
Carbon dioxide | CO2 | 1 | 1 | 1
Methane | CH4 | 3 | 1 | 3
Ethene | C2H4 | 3 | 1 | 3
Ethane | C2H6 | 3 | 1 | 3
Ethyne (Acetylene) | C2H2 | 5 | 2 | 10
Rating | Number
B | 3
Scoring criteria |  | Weighting | Gas scores | Weighted scores | DGAF
Hydrogen | H2 | 2 | 1 | 2 | 1.3333 | 2006-11-30
Carbon monoxide | CO | 1 | 2 | 2
Carbon dioxide | CO2 | 1 | 1 | 1
Methane | CH4 | 3 | 1 | 3
Ethene | C2H4 | 3 | 1 | 3
Ethane | C2H6 | 3 | 1 | 3
Ethyne (Acetylene) | C2H2 | 5 | 2 | 10
Rating | Number
B | 3
Scoring criteria |  | Weighting | Gas scores | Weighted scores | DGAF
Hydrogen | H2 | 2 | 1 | 2 | 1.3333 | 2007-04-19
Carbon monoxide | CO | 1 | 2 | 2
Carbon dioxide | CO2 | 1 | 1 | 1
Methane | CH4 | 3 | 1 | 3
Ethene | C2H4 | 3 | 1 | 3
Ethane | C2H6 | 3 | 1 | 3
Ethyne (Acetylene) | C2H2 | 5 | 2 | 10
Rating | Number
B | 3
Scoring criteria |  | Weighting | Gas scores | Weighted scores | DGAF
Hydrogen | H2 | 2 | 1 | 2 | 1.3333 | 2007-11-08
Carbon monoxide | CO | 1 | 2 | 2
Carbon dioxide | CO2 | 1 | 1 | 1
Methane | CH4 | 3 | 1 | 3
Ethene | C2H4 | 3 | 1 | 3
Ethane | C2H6 | 3 | 1 | 3
Ethyne (Acetylene) | C2H2 | 5 | 2 | 10
Rating | Number
B | 3
Scoring criteria |  | Weighting | Gas scores | Weighted scores | DGAF
Hydrogen | H2 | 2 | 1 | 2 | 1.2778 | 2008-03-14
Carbon monoxide | CO | 1 | 1 | 1
Carbon dioxide | CO2 | 1 | 1 | 1
Methane | CH4 | 3 | 1 | 3
Ethene | C2H4 | 3 | 1 | 3
Ethane | C2H6 | 3 | 1 | 3
Ethyne (Acetylene) | C2H2 | 5 | 2 | 10
Rating | Number
B | 3
Scoring criteria |  | Weighting | Gas scores | Weighted scores | DGAF
Hydrogen | H2 | 2 | 1 | 2 | 1.3333 | 2008-09-04
Carbon monoxide | CO | 1 | 2 | 2
Carbon dioxide | CO2 | 1 | 1 | 1
Methane | CH4 | 3 | 1 | 3
Ethene | C2H4 | 3 | 1 | 3
Ethane | C2H6 | 3 | 1 | 3
Ethyne (Acetylene) | C2H2 | 5 | 2 | 10
Rating | Number
B | 3
Scoring criteria |  | Weighting | Gas scores | Weighted scores | DGAF
Hydrogen | H2 | 2 | 1 | 2 | 1.3333 | 2009-02-25
Carbon monoxide | CO | 1 | 2 | 2
Carbon dioxide | CO2 | 1 | 1 | 1
Methane | CH4 | 3 | 1 | 3
Ethene | C2H4 | 3 | 1 | 3
Ethane | C2H6 | 3 | 1 | 3
Ethyne (Acetylene) | C2H2 | 5 | 2 | 10
Rating | Number
B | 3
Scoring criteria |  | Weighting | Gas scores | Weighted scores | DGAF
Hydrogen | H2 | 2 | 1 | 2 | 1.3333 | 2009-10-09
Carbon monoxide | CO | 1 | 2 | 2
Carbon dioxide | CO2 | 1 | 1 | 1
Methane | CH4 | 3 | 1 | 3
Ethene | C2H4 | 3 | 1 | 3
Ethane | C2H6 | 3 | 1 | 3
Ethyne (Acetylene) | C2H2 | 5 | 2 | 10
Rating | Number
B | 3

## 2-FAL
Furfural concentration test rating
Sample | [2-FAL] ppm | Rating Code | Number
1997-01-02 | 0 | A | 4 | Rating Code | Number | Int
1997-06-25 | 0 | A | 4 | A | 4 | 0.1
1997-12-22 | 0.05 | A | 4 | B | 3 | 0.25
1999-02-11 | 0 | A | 4 | C | 2 | 0.5
1999-07-23 | 0 | A | 4 | D | 1 | 1
2000-02-11 | 0 | A | 4 | E | 0 | >=1
2000-10-09 | 0 | A | 4
2001-02-16 | 0 | A | 4
2001-08-07 | 0 | A | 4
2002-01-18 | 0 | A | 4
2003-01-15 | 0 | A | 4
2004-02-05 | 0 | A | 4
2005-02-10 | 0 | A | 4
2006-01-31 | 0 | A | 4
2007-04-19 | 0.02 | A | 4
2008-03-14 | 0.02 | A | 4
2009-02-25 | 0 | A | 4
2010-07-08 | 0 | A | 4

## PF
Power Factor Rating
|  | Rating Code | Max
Rating Code | Number | A | 0.5
D | 1 | B | 0.7
|  | C | 1
Sample | Maximum Power Factor | D | 2
1997-05-19 | 1 | E | >=2
1998-05-19 | 1
1999-03-18 | 1
2000-06-30 | 1
2001-08-10 | 1
2002-06-19 | 1
2002-12-23 | 1
2003-04-24 | 1
2004-05-27 | 1
2005-05-30 | 1
2006-11-16 | 1
2007-05-03 | 1
2008-07-23 | 1
2009-12-09 | 1
2010-05-20 | 1
2010-12-16 | 1
2012-05-11 | 1
2014-01-14 | 1
2015-08-26 14:39 | 1
2016-05-06 09:30 | 1

## GOT
Evaluation of oil quality
Oil Sample Analysis Results | Results from oil analysis
Date | 2015-09-03 09:00 | 2014-01-14 | 2012-06-26 | 2010-12-02 | 2010-07-08 | 2009-10-09 | 2009-02-25 | 2008-09-04 | 2008-03-14 | 2007-11-08 | 2007-04-19 | 2006-11-30 | 2006-01-31 | 2005-07-13 | 2005-02-10 | 2004-08-26 | 2004-02-05 | 2003-07-17 | 2003-01-15 | 2002-01-18 | 2001-08-07 | 2001-02-16 | 2000-10-09 | 2000-02-11 | 1999-07-23 | 1999-02-11 | 1997-12-22 | 1997-06-25 | 1997-01-02 | 1996-07-01
Breakdown voltage [kV] | 92 | 65.4 | 92.1 | 58.7 | 69.7 | 72.2 | 90.1 | 76.6 | 82.3 | 64.4 | 82.2 | 84 | 78 | 70.5 | 76.3 | 72.2 | 73.2 | 82.8 | 79.2 | 76.7 | 57.9 | 67.1 | 79.4 | 79.2 | 77.4 | 77.4 | 88.8 | 84.4 | 84.4 | 84.4
Water content [mg/kg] | 8 | 5.1 | 9.7 | 7.4 | 12.4 | 10.2 | 5.4 | 8.7 | 9.4 | 9.9 | 11 | 8.2 | 8.8 | 14.8 | 7.6 | 7.6 | 8 | 4.6 | 5.7 | 5 | 7.2 | 6.4 | 7 | 7.4 | 15.7 | 4.2 | 6.7 | 11.1 | 8.2 | 9.7
Acidity [mg KOH/g] | 0.04 | 0.038 | 0.034 | 0.017 | 0.017 | 0.024 | 0.024 | 0.022 | 0.022 | 0.025 | 0.025 | 0.022 | 0.022 | 0.084 | 0.084 | 0.028 | 0.028 | 0.036 | 0.036 | 0.022 | 0.014 | 0.014 | 0.023 | 0.023 | 0.005 | 0.005 | 0.013 | 0.008 | 0.008 | 0.008
Color | 2 | 1.5 | 1.5 | 1.75 | 1.75 | 1.25 | 1.25 | 1.25 | 1.25 | 1.25 | 1.25 | 1.25 | 1.25 | 1.25 | 1.25 | 1.25 | 1.25 | 1.25 | 1.25 | 1.25 | 1.25 | 1.25 | 1.25 | 1.25 | 1.25 | 1.25 | 1 | 1.25 | 1.25 | 1.25
Interfacial tension | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.4 | 25.4 | 25.6 | 25.6 | 26.1 | 26.1 | 25.9 | 25.9 | 25.9 | 25.9 | 25.9 | 25.9 | 28.2 | 28.2 | 25.5 | 29.7 | 29.7 | 38.4 | 38.4 | 28.2 | 28.2 | 30.6 | 31.6 | 31.6 | 31.6
[6 empty] | DATA.XL | TENS_DISRU | TEOR_AGUA | IND_ACIDEZ | COR,NUM | TENS_INTER
[6 empty] | 2015-09-03 09:00 | 92 | 8 | 0.04 | 2
[6 empty] | 2014-01-14 | 65.4 | 5.1 | 0.038 | 1.5
[6 empty] | 2012-06-26 | 92.1 | 9.7 | 0.034 | 1.5
[6 empty] | 2010-12-02 | 58.7 | 7.4
[6 empty] | 2010-07-08 | 69.7 | 12.4 | 0.017 | 1.75 | 25.7
[6 empty] | 2009-10-09 | 72.2 | 10.2 | #N/A | #N/A | #N/A
[6 empty] | 2009-02-25 | 90.1 | 5.4 | 0.024 | 1.25 | 25.4
[6 empty] | 2008-09-04 | 76.6 | 8.7 | #N/A | #N/A | #N/A
[6 empty] | 2008-03-14 | 82.3 | 9.4 | 0.022 | 1.25 | 25.6
[6 empty] | 2007-11-08 | 64.4 | 9.9 | #N/A | #N/A | #N/A
[6 empty] | 2007-04-19 | 82.2 | 11 | 0.025 | 1.25 | 26.1
[6 empty] | 2006-11-30 | 84 | 8.2 | #N/A | #N/A | #N/A
[6 empty] | 2006-01-31 | 78 | 8.8 | 0.022 | 1.25 | 25.9
[6 empty] | 2005-07-13 | 70.5 | 14.8 | #N/A | #N/A | #N/A
[6 empty] | 2005-02-10 | 76.3 | 7.6 | 0.084 | 1.25 | 25.9
[6 empty] | 2004-08-26 | 72.2 | 7.6 | #N/A | #N/A | #N/A
[6 empty] | 2004-02-05 | 73.2 | 8 | 0.028 | 1.25 | 25.9
[6 empty] | 2003-07-17 | 82.8 | 4.6 | #N/A | #N/A | #N/A
[6 empty] | 2003-01-15 | 79.2 | 5.7 | 0.036 | 1.25 | 28.2
[6 empty] | 2002-01-18 | 76.7 | 5 | 0.022 | 1.25 | 25.5
[6 empty] | 2001-08-07 | 57.9 | 7.2 | #N/A | #N/A | #N/A
[6 empty] | 2001-02-16 | 67.1 | 6.4 | 0.014 | 1.25 | 29.7
[6 empty] | 2000-10-09 | 79.4 | 7 | #N/A | #N/A | #N/A
[6 empty] | 2000-02-11 | 79.2 | 7.4 | 0.023 | 1.25 | 38.4
[6 empty] | 1999-07-23 | #N/A | 15.7 | #N/A | #N/A | #N/A
[6 empty] | 1999-02-11 | 77.4 | 4.2 | 0.005 | 1.25 | 28.2
[6 empty] | 1997-12-22 | 88.8 | 6.7 | 0.013 | 1 | 30.6
[6 empty] | 1997-06-25 | #N/A | 11.1 | #N/A | #N/A | #N/A
[6 empty] | 1997-01-02 | 84.4 | 8.2 | 0.008 | 1.25 | 31.6
[6 empty] | 1996-07-01 | #N/A | 9.7 | #N/A | #N/A | #N/A

## OQF
| Score | Weight | SxW | OQF | 1.1667 | 1996-07-01
BDV | 1 | 3 | 3 |  |  |  |  | Score | Weight | SxW | OQF | 1.5 | 2010-07-08
Moisture | 1 | 4 | 4 |  |  |  | BDV | 1 | 3 | 3
Acidity | 1 | 1 | 1 |  |  |  | Moisture | 1 | 4 | 4
Color | 1 | 2 | 2 | Final rating | 4 |  | Acidity | 1 | 1 | 1
IFT | 2 | 2 | 4 |  |  |  | Color | 2 | 2 | 4 | Final rating | 2
[7 empty] | IFT | 3 | 2 | 6
| Score | Weight | SxW | OQF | 1.1667 | 1997-01-02
BDV | 1 | 3 | 3 |  |  |  |  | Score | Weight | SxW | OQF | 1.5 | 2010-12-02
Moisture | 1 | 4 | 4 |  |  |  | BDV | 1 | 3 | 3
Acidity | 1 | 1 | 1 |  |  |  | Moisture | 1 | 4 | 4
Color | 1 | 2 | 2 | Final rating | 4 |  | Acidity | 1 | 1 | 1
IFT | 2 | 2 | 4 |  |  |  | Color | 2 | 2 | 4 | Final rating | 2
[7 empty] | IFT | 3 | 2 | 6
| Score | Weight | SxW | OQF | 1.1667 | 1997-06-25
BDV | 1 | 3 | 3 |  |  |  |  | Score | Weight | SxW | OQF | 1.5 | 2012-06-26
Moisture | 1 | 4 | 4 |  |  |  | BDV | 1 | 3 | 3
Acidity | 1 | 1 | 1 |  |  |  | Moisture | 1 | 4 | 4
Color | 1 | 2 | 2 | Final rating | 4 |  | Acidity | 1 | 1 | 1
IFT | 2 | 2 | 4 |  |  |  | Color | 2 | 2 | 4 | Final rating | 2
[7 empty] | IFT | 3 | 2 | 6
| Score | Weight | SxW | OQF | 1.1667 | 1997-12-22
BDV | 1 | 3 | 3 |  |  |  |  | Score | Weight | SxW | OQF | 1.5 | 2014-01-14
Moisture | 1 | 4 | 4 |  |  |  | BDV | 1 | 3 | 3
Acidity | 1 | 1 | 1 |  |  |  | Moisture | 1 | 4 | 4
Color | 1 | 2 | 2 | Final rating | 4 |  | Acidity | 1 | 1 | 1
IFT | 2 | 2 | 4 |  |  |  | Color | 2 | 2 | 4 | Final rating | 2
[7 empty] | IFT | 3 | 2 | 6
| Score | Weight | SxW | OQF | 1.3333 | 1999-02-11
BDV | 1 | 3 | 3 |  |  |  |  | Score | Weight | SxW | OQF | 1.6667 | 2015-09-03 09:00
Moisture | 1 | 4 | 4 |  |  |  | BDV | 1 | 3 | 3
Acidity | 1 | 1 | 1 |  |  |  | Moisture | 1 | 4 | 4
Color | 1 | 2 | 2 | Final rating | 3 |  | Acidity | 1 | 1 | 1
IFT | 3 | 2 | 6 |  |  |  | Color | 3 | 2 | 6 | Final rating | 2
[7 empty] | IFT | 3 | 2 | 6
| Score | Weight | SxW | OQF | 1.3333 | 1999-07-23
BDV | 1 | 3 | 3
Moisture | 1 | 4 | 4
Acidity | 1 | 1 | 1
Color | 1 | 2 | 2 | Final rating | 3
IFT | 3 | 2 | 6
| Score | Weight | SxW | OQF | 1 | 2000-02-11
BDV | 1 | 3 | 3
Moisture | 1 | 4 | 4
Acidity | 1 | 1 | 1
Color | 1 | 2 | 2 | Final rating | 4
IFT | 1 | 2 | 2
| Score | Weight | SxW | OQF | 1 | 2000-10-09
BDV | 1 | 3 | 3 | [12 empty] | Voltage level | 72.5 | Score | Weight
Moisture | 1 | 4 | 4
Acidity | 1 | 1 | 1 | [12 empty] | Breakdown Voltage [kV] | >50 | 1 | 3
Color | 1 | 2 | 2 | Final rating | 4 | [11 empty] | 50 | 2
IFT | 1 | 2 | 2 | [13 empty] | 40 | 3
[17 empty] | 30 | 4
[16 empty] | Moisture | 20 | 1 | 4
[17 empty] | 30 | 2
[17 empty] | 40 | 3
| Score | Weight | SxW | OQF | 1.3333 | 2001-02-16 | [10 empty] | >40 | 4
BDV | 1 | 3 | 3 | [12 empty] | Acidity (mg KOH/g) | 0.05 | 1 | 1
Moisture | 1 | 4 | 4 | [13 empty] | 0.1 | 2
Acidity | 1 | 1 | 1 | [13 empty] | 0.2 | 3
Color | 1 | 2 | 2 | Final rating | 3 | [11 empty] | >0.2 | 4
IFT | 3 | 2 | 6 | [12 empty] | Color | 1.5 | 1 | 2
[17 empty] | 2 | 2
[17 empty] | 2.5 | 3
[17 empty] | >2,5 | 4
[16 empty] | Interfacial tension [mN/m] | >35 | 1 | 2
| Score | Weight | SxW | OQF | 1.3333 | 2001-08-07 | [10 empty] | 35 | 2
BDV | 1 | 3 | 3 | [10 empty] | 1.5 | 2010 |  | 30 | 3
Moisture | 1 | 4 | 4 | [10 empty] | 1.5 | 2012 |  | 25 | 4
Acidity | 1 | 1 | 1 | [10 empty] | 1.5 | 2014
Color | 1 | 2 | 2 | Final rating | 3 | [8 empty] | 1.5 | 2015
IFT | 3 | 2 | 6 | [10 empty] | 1.6667 | 2016
| Score | Weight | SxW | OQF | 1.3333 | 2002-01-18
BDV | 1 | 3 | 3
Moisture | 1 | 4 | 4
Acidity | 1 | 1 | 1
Color | 1 | 2 | 2 | Final rating | 3
IFT | 3 | 2 | 6
| Score | Weight | SxW | OQF | 1.3333 | 2003-01-15
BDV | 1 | 3 | 3
Moisture | 1 | 4 | 4
Acidity | 1 | 1 | 1
Color | 1 | 2 | 2 | Final rating | 3
IFT | 3 | 2 | 6
| Score | Weight | SxW | OQF | 1.3333 | 2003-07-17
BDV | 1 | 3 | 3
Moisture | 1 | 4 | 4
Acidity | 1 | 1 | 1
Color | 1 | 2 | 2 | Final rating | 3
IFT | 3 | 2 | 6
| Score | Weight | SxW | OQF | 1.3333 | 2004-02-05
BDV | 1 | 3 | 3
Moisture | 1 | 4 | 4
Acidity | 1 | 1 | 1
Color | 1 | 2 | 2 | Final rating | 3
IFT | 3 | 2 | 6
| Score | Weight | SxW | OQF | 1.3333 | 2004-08-26
BDV | 1 | 3 | 3
Moisture | 1 | 4 | 4
Acidity | 1 | 1 | 1
Color | 1 | 2 | 2 | Final rating | 3
IFT | 3 | 2 | 6
| Score | Weight | SxW | OQF | 1.4167 | 2005-02-10
BDV | 1 | 3 | 3
Moisture | 1 | 4 | 4
Acidity | 2 | 1 | 2
Color | 1 | 2 | 2 | Final rating | 3
IFT | 3 | 2 | 6
| Score | Weight | SxW | OQF | 1.4167 | 2005-07-13
BDV | 1 | 3 | 3
Moisture | 1 | 4 | 4
Acidity | 2 | 1 | 2
Color | 1 | 2 | 2 | Final rating | 3
IFT | 3 | 2 | 6
| Score | Weight | SxW | OQF | 1.3333 | 2006-01-31
BDV | 1 | 3 | 3
Moisture | 1 | 4 | 4
Acidity | 1 | 1 | 1
Color | 1 | 2 | 2 | Final rating | 3
IFT | 3 | 2 | 6
| Score | Weight | SxW | OQF | 1.3333 | 2006-11-30
BDV | 1 | 3 | 3
Moisture | 1 | 4 | 4
Acidity | 1 | 1 | 1
Color | 1 | 2 | 2 | Final rating | 3
IFT | 3 | 2 | 6
| Score | Weight | SxW | OQF | 1.3333 | 2007-04-19
BDV | 1 | 3 | 3
Moisture | 1 | 4 | 4
Acidity | 1 | 1 | 1
Color | 1 | 2 | 2 | Final rating | 3
IFT | 3 | 2 | 6
| Score | Weight | SxW | OQF | 1.3333 | 2007-11-08
BDV | 1 | 3 | 3
Moisture | 1 | 4 | 4
Acidity | 1 | 1 | 1
Color | 1 | 2 | 2 | Final rating | 3
IFT | 3 | 2 | 6
| Score | Weight | SxW | OQF | 1.3333 | 2008-03-14
BDV | 1 | 3 | 3
Moisture | 1 | 4 | 4
Acidity | 1 | 1 | 1
Color | 1 | 2 | 2 | Final rating | 3
IFT | 3 | 2 | 6
| Score | Weight | SxW | OQF | 1.3333 | 2008-09-04
BDV | 1 | 3 | 3
Moisture | 1 | 4 | 4
Acidity | 1 | 1 | 1
Color | 1 | 2 | 2 | Final rating | 3
IFT | 3 | 2 | 6
| Score | Weight | SxW | OQF | 1.3333 | 2009-02-25
BDV | 1 | 3 | 3
Moisture | 1 | 4 | 4
Acidity | 1 | 1 | 1
Color | 1 | 2 | 2 | Final rating | 3
IFT | 3 | 2 | 6
| Score | Weight | SxW | OQF | 1.3333 | 2009-10-09
BDV | 1 | 3 | 3
Moisture | 1 | 4 | 4
Acidity | 1 | 1 | 1
Color | 1 | 2 | 2 | Final rating | 3
IFT | 3 | 2 | 6

## Load
Load Factor Rating | [10 empty] | SE1 | SE2 | SE3 | SE4 | SE5 | SE6 | SE7 | SE8 | SE9
|  | Month | Load peak | Si/Sb | Rating Code |  |  |  | 2011 | jan | 183 | 306 | 190 | 103 | 158 | 129 | 90 | 96 | 104 | 2016-01-01 | 86 | 173 | 66 | 29 | 93 | 73 | 88 | 70 | 89
| LF | 1 | 190 | 0.55882 | A |  | Number of instances |  |  | fev | 165 | 326 | 185 | 88 | 148 | 132 | 92 | 100 | 103 | 2016-01-02 | 102 | 148 | 82 | 26 | 106 | 88 | 99 | 56 | 67
| 3.849 | 2 | 185 | 0.54412 |  | N0 | 163 |  |  | mar | 166 | 254 | 181 | 51 | 138 | 93 | 76 | 103 | 126 | 2016-01-03 | 96 | 189 | 58 | 84 | 79 | 84 | 88 | 65 | 87
|  | 3 | 181 | 0.53235 | Number | N1 | 29 |  |  | abril | 156 | 236 | 185 | 41 | 119 | 109 | 73 | 109 | 90 | 2016-01-04 | 124 | 186 | 58 | 69 | 103 | 132 | 82 | 68 | 43
| Sb [MVA] | 4 | 185 | 0.54412 | 4 | N2 | 0 |  |  | maio | 157 | 256 | 150 | 46 | 123 | 87 | 86 | 107 | 134 | 2016-01-05 | 128 | 191 | 57 | 39 | 100 | 136 | 89 | 58 | 73
| 340 | 5 | 150 | 0.44118 |  | N3 | 0 |  |  | jun | 148 | 288 | 129 | 49 | 126 | 125 | 73 | 96 | 115 | 2016-01-06 | 132 | 222 | 50 | 43 | 72 | 141 | 99 | 50 | 37
|  | 6 | 129 | 0.37941 |  | N4 | 0 |  |  | jul | 151 | 332 | 91 | 39 | 129 | 91 | 79 | 85 | 106 | 2016-01-07 | 135 | 185 | 50 | 48 | 85 | 134 | 90 | 57 | 71
|  | 7 | 91 | 0.26765 | [5 empty] | agosto | 151 | 270 | 116 | 44 | 132 | 110 | 82 | 68 | 127 | 2016-01-08 | 126 | 185 | 81 | 55 | 115 | 139 | 98 | 63 | 64
|  | 8 | 116 | 0.34118 | [5 empty] | set | 164 | 262 | 133 | 32 | 141 | 88 | 77 | 91 | 97 | 2016-01-09 | 102 | 155 | 63 | 80 | 76 | 101 | 92 | 49 | 76
|  | 9 | 133 | 0.39118 |  | Rating Code | Description | Rating Code |  | out | 175 | 280 | 120 | 64 | 133 | 118 | 75 | 90 | 100 | 2016-01-10 | 96 | 181 | 51 | 85 | 98 | 85 | 88 | 64 | 84 |  | 140 | 229 | 110 | 85 | 128 | 141 | 107 | 70 | 90
|  | 10 | 120 | 0.35294 |  | A | >=3.5 | 4 |  | nov | 171 | 270 | 123 | 73 | 145 | 99 | 86 | 73 | 82 | 2016-01-11 | 133 | 229 | 82 | 85 | 82 | 132 | 92 | 60 | 84 |  | 143 | 238 | 132 | 91 | 124 | 149 | 100 | 69 | 102
|  | 11 | 123 | 0.36176 |  | B | 3.5 | 3 |  | dez | 156 | 280 | 135 | 57 | 140 | 114 | 78 | 77 | 92 | 2016-01-12 | 132 | 207 | 84 | 80 | 128 | 137 | 93 | 63 | 59 |  | 136 | 219 | 96 | 96 | 71 | 118 | 137 | 101 | 73
|  | 12 | 135 | 0.39706 |  | C | 2.5 | 2 | [11 empty] | 2016-01-13 | 140 | 201 | 82 | 42 | 94 | 136 | 96 | 39 | 68 |  | 133 | 196 | 109 | 79 | 109 | 134 | 109 | 70 | 92
|  | 1 | 156 | 0.45882 |  | D | 1.5 | 1 | [11 empty] | 2016-01-14 | 127 | 199 | 66 | 47 | 97 | 135 | 89 | 63 | 74 |  | 122 | 247 | 85 | 97 | 111 | 132 | 89 | 68 | 100
|  | 2 | 112 | 0.32941 |  | E | 0.5 | 0 | [11 empty] | 2016-01-15 | 130 | 191 | 82 | 59 | 99 | 131 | 89 | 52 | 80 |  | 128 | 242 | 82 | 66 | 108 | 125 | 106 | 71 | 83
|  | 3 | 107 | 0.31471 |  |  |  |  | 2012 | jan | 182 | 324 | 156 | 53 | 147 | 129 | 85 | 90 | 158 | 2016-01-16 | 109 | 164 | 90 | 58 | 97 | 100 | 86 | 42 | 38 |  | 153 | 255 | 87 | 52 | 117 | 130 | 111 | 82 | 151
|  | 4 | 145 | 0.42647 | [5 empty] | fev | 187 | 307 | 112 | 45 | 137 | 99 | 87 | 91 | 114 | 2016-01-17 | 115 | 156 | 110 | 48 | 110 | 90 | 99 | 30 | 81 |  | 143 | 200 | 60 | 52 | 111 | 126 | 107 | 61 | 83
|  | 5 | 130 | 0.38235 | [5 empty] | mar | 162 | 280 | 107 | 44 | 127 | 90 | 73 | 67 | 162 | 2016-01-18 | 137 | 205 | 82 | 31 | 120 | 136 | 102 | 57 | 70 |  | 152 | 228 | 108 | 78 | 120 | 127 | 115 | 56 | 87
|  | 6 | 134 | 0.39412 | [5 empty] | abril | 156 | 269 | 145 | 70 | 129 | 91 | 74 | 78 | 96 | 2016-01-19 | 132 | 199 | 80 | 71 | 118 | 140 | 94 | 62 | 48 |  | 131 | 243 | 120 | 60 | 113 | 126 | 109 | 67 | 110
|  | 7 | 131 | 0.38529 | [5 empty] | maio | 152 | 242 | 130 | 46 | 113 | 89 | 70 | 72 | 102 | 2016-01-20 | 139 | 183 | 80 | 66 | 124 | 140 | 99 | 55 | 67 |  | 136 | 283 | 109 | 50 | 128 | 148 | 103 | 84 | 118
|  | 8 | 113 | 0.33235 | [5 empty] | jun | 160 | 225 | 134 | 37 | 122 | 99 | 82 | 70 | 125 | 2016-01-21 | 140 | 183 | 90 | 23 | 122 | 137 | 99 | 54 | 73 |  | 149 | 254 | 114 | 84 | 122 | 150 | 110 | 91 | 108
|  | 9 | 110 | 0.32353 | [5 empty] | jul | 162 | 287 | 131 | 43 | 120 | 87 | 97 | 67 | 211 | 2016-01-22 | 136 | 183 | 88 | 44 | 126 | 134 | 92 | 58 | 59
|  | 10 | 118 | 0.34706 | [5 empty] | agosto | 165 | 236 | 113 | 57 | 122 | 95 | 105 | 67 | 173 | 2016-01-23 | 109 | 167 | 85 | 59 | 69 | 95 | 103 | 46 | 62
|  | 11 | 134 | 0.39412 | [5 empty] | set | 172 | 250 | 110 | 65 | 129 | 122 | 108 | 71 | 185 | 2016-01-24 | 100 | 147 | 63 | 57 | 109 | 76 | 91 | 56 | 90
|  | 12 | 137 | 0.40294 | [5 empty] | out | 144 | 261 | 118 | 64 | 121 | 107 | 112 | 75 | 168 | 2016-01-25 | 132 | 190 | 81 | 33 | 117 | 131 | 97 | 59 | 89
|  | 1 | 148 | 0.43529 | [5 empty] | nov | 151 | 284 | 134 | 76 | 133 | 96 | 98 | 124 | 136 | 2016-01-26 | 131 | 200 | 87 | 32 | 112 | 130 | 105 | 59 | 42
|  | 2 | 108 | 0.31765 | [5 empty] | dez | 194 | 314 | 137 | 79 | 148 | 104 | 94 | 95 | 121 | 2016-01-27 | 132 | 201 | 98 | 37 | 121 | 132 | 107 | 42 | 57
|  | 3 | 106 | 0.31176 | [15 empty] | 2016-01-28 | 132 | 217 | 88 | 39 | 113 | 132 | 98 | 52 | 67
|  | 4 | 107 | 0.31471 | [15 empty] | 2016-01-29 | 126 | 177 | 64 | 20 | 90 | 128 | 93 | 59 | 63
|  | 5 | 117 | 0.34412 |  |  |  |  | 2013 | jan | 182 | 283 | 148 | 80 | 141 | 124 | 88 | 68 | 123 | 2016-01-30 | 119 | 167 | 88 | 27 | 92 | 100 | 93 | 44 | 66
|  | 6 | 170 | 0.5 | [5 empty] | fev | 168 | 273 | 108 | 78 | 135 | 93 | 99 | 68 | 129 | 2016-01-31 | 108 | 189 | 80 | 24 | 63 | 84 | 95 | 42 | 38 | 140 | 229 | 110 | 85 | 128 | 141 | 107 | 70 | 90
|  | 7 | 112 | 0.32941 | [5 empty] | mar | 149 | 266 | 106 | 96 | 125 | 115 | 104 | 69 | 96 | 2016-02-01 | 125 | 206 | 72 | 26 | 101 | 128 | 93 | 58 | 39
|  | 8 | 122 | 0.35882 | [5 empty] | abril | 140 | 215 | 107 | 92 | 115 | 110 | 91 | 61 | 102 | 2016-02-02 | 120 | 190 | 46 | 52 | 66 | 130 | 90 | 50 | 37
|  | 9 | 106 | 0.31176 | [5 empty] | maio | 130 | 246 | 117 | 56 | 106 | 92 | 98 | 60 | 84 | 2016-02-03 | 125 | 202 | 72 | 65 | 84 | 128 | 88 | 53 | 77
|  | 10 | 131 | 0.38529 | [5 empty] | jun | 153 | 229 | 170 | 86 | 114 | 91 | 139 | 61 | 80 | 2016-02-04 | 134 | 195 | 56 | 64 | 90 | 129 | 90 | 62 | 49
|  | 11 | 139 | 0.40882 | [5 empty] | jul | 162 | 267 | 112 | 40 | 123 | 112 | 104 | 75 | 113 | 2016-02-05 | 126 | 206 | 79 | 35 | 124 | 126 | 97 | 56 | 50
|  | 12 | 152 | 0.44706 | [5 empty] | agosto | 149 | 211 | 122 | 41 | 123 | 100 | 113 | 80 | 86 | 2016-02-06 | 97 | 186 | 73 | 54 | 90 | 100 | 92 | 57 | 84
|  | 1 | 137 | 0.40294 | [5 empty] | set | 148 | 254 | 106 | 57 | 133 | 105 | 111 | 90 | 86 | 2016-02-07 | 109 | 157 | 132 | 30 | 95 | 82 | 96 | 63 | 82
|  | 2 | 180 | 0.52941 | [5 empty] | out | 143 | 251 | 131 | 74 | 129 | 88 | 102 | 90 | 100 | 2016-02-08 | 126 | 190 | 106 | 40 | 92 | 116 | 100 | 54 | 85
|  | 3 | 141 | 0.41471 | [5 empty] | nov | 165 | 289 | 139 | 78 | 141 | 96 | 107 | 102 | 89 | 2016-02-09 | 99 | 167 | 57 | 53 | 96 | 86 | 93 | 69 | 86
|  | 4 | 115 | 0.33824 | [5 empty] | dez | 188 | 321 | 152 | 82 | 142 | 103 | 101 | 73 | 127 | 2016-02-10 | 123 | 198 | 76 | 28 | 63 | 140 | 94 | 67 | 85
|  | 5 | 138 | 0.40588 | [15 empty] | 2016-02-11 | 130 | 183 | 82 | 45 | 90 | 137 | 87 | 65 | 77
|  | 6 | 152 | 0.44706 | [15 empty] | 2016-02-12 | 119 | 209 | 58 | 63 | 79 | 141 | 91 | 67 | 85
|  | 7 | 135 | 0.39706 |  |  |  |  | 2014 | jan | 166 | 251 | 137 | 101 | 135 | 98 | 100 | 102 | 115 | 2016-02-13 | 94 | 195 | 68 | 77 | 84 | 107 | 89 | 65 | 81
|  | 8 | 133 | 0.39118 | [5 empty] | fev | 144 | 250 | 180 | 103 | 140 | 134 | 113 | 66 | 108 | 2016-02-14 | 96 | 186 | 65 | 79 | 99 | 94 | 78 | 66 | 102
|  | 9 | 122 | 0.35882 | [5 empty] | mar | 126 | 231 | 141 | 78 | 128 | 96 | 102 | 63 | 97 | 2016-02-15 | 120 | 211 | 68 | 76 | 91 | 136 | 85 | 42 | 96
|  | 10 | 148 | 0.43529 | [5 empty] | abril | 120 | 202 | 115 | 87 | 114 | 92 | 99 | 64 | 76 | 2016-02-16 | 141 | 222 | 80 | 91 | 48 | 136 | 81 | 64 | 85
|  | 11 | 166 | 0.48824 | [5 empty] | maio | 121 | 223 | 138 | 55 | 109 | 85 | 95 | 68 | 87 | 2016-02-17 | 143 | 229 | 100 | 61 | 37 | 143 | 85 | 46 | 57
|  | 12 | 137 | 0.40294 | [5 empty] | jun | 128 | 234 | 152 | 60 | 117 | 87 | 95 | 65 | 88 | 2016-02-18 | 135 | 217 | 65 | 66 | 62 | 135 | 80 | 59 | 78
|  | 1 | 156 | 0.45882 | [5 empty] | jul | 139 | 225 | 135 | 68 | 119 | 91 | 103 | 59 | 101 | 2016-02-19 | 133 | 206 | 55 | 61 | 49 | 134 | 85 | 62 | 54
|  | 2 | 188 | 0.55294 | [5 empty] | agosto | 138 | 216 | 133 | 76 | 128 | 78 | 99 | 59 | 90 | 2016-02-20 | 105 | 162 | 65 | 73 | 58 | 100 | 75 | 34 | 21
|  | 3 | 146 | 0.42941 | [5 empty] | set | 161 | 265 | 122 | 43 | 131 | 88 | 93 | 65 | 81 | 2016-02-21 | 117 | 143 | 85 | 46 | 68 | 86 | 85 | 41 | 48
|  | 4 | 124 | 0.36471 | [5 empty] | out | 142 | 264 | 148 | 121 | 126 | 91 | 92 | 66 | 79 | 2016-02-22 | 132 | 216 | 65 | 59 | 47 | 130 | 87 | 58 | 24
|  | 5 | 120 | 0.35294 | [5 empty] | nov | 142 | 249 | 166 | 96 | 131 | 118 | 92 | 63 | 90 | 2016-02-23 | 111 | 199 | 118 | 46 | 104 | 136 | 98 | 64 | 39
|  | 6 | 165 | 0.48529 | [5 empty] | dez | 151 | 250 | 137 | 74 | 139 | 107 | 96 | 71 | 121 | 2016-02-24 | 121 | 238 | 47 | 58 | 86 | 139 | 77 | 29 | 78
|  | 7 | 142 | 0.41765 | [15 empty] | 2016-02-25 | 140 | 207 | 77 | 29 | 111 | 149 | 86 | 48 | 35
|  | 8 | 116 | 0.34118 | [15 empty] | 2016-02-26 | 119 | 214 | 46 | 72 | 75 | 141 | 79 | 58 | 76
|  | 9 | 114 | 0.33529 |  |  |  |  | 2015 | jan | 165 | 296 | 156 | 59 | 154 | 114 | 108 | 67 | 95 | 2016-02-27 | 105 | 190 | 74 | 58 | 98 | 108 | 92 | 47 | 91
|  | 10 | 118 | 0.34706 | [5 empty] | fev | 149 | 279 | 188 | 67 | 150 | 124 | 118 | 73 | 98 | 2016-02-28 | 100 | 171 | 62 | 62 | 108 | 94 | 79 | 43 | 92
|  | 11 | 138 | 0.40588 | [5 empty] | mar | 129 | 256 | 146 | 61 | 129 | 109 | 91 | 69 | 80 | 2016-02-29 | 134 | 205 | 81 | 38 | 99 | 135 | 90 | 60 | 90 | 143 | 238 | 132 | 91 | 124 | 149 | 100 | 69 | 102
|  | 12 | 103 | 0.30294 | [5 empty] | abril | 146 | 233 | 124 | 68 | 112 | 116 | 89 | 66 | 100 | 2016-03-01 | 124 | 212 | 68 | 65 | 101 | 130 | 101 | 52 | 20
|  | 1 | 110 | 0.32353 | [5 empty] | maio | 125 | 214 | 120 | 62 | 114 | 109 | 98 | 71 | 117 | 2016-03-02 | 123 | 199 | 55 | 67 | 81 | 134 | 90 | 30 | 42
|  | 2 | 132 | 0.38824 | [5 empty] | jun | 148 | 239 | 165 | 55 | 122 | 103 | 97 | 69 | 68 | 2016-03-03 | 119 | 196 | 41 | 49 | 88 | 129 | 85 | 55 | 61
|  | 3 | 96 | 0.28235 | [5 empty] | jul | 139 | 242 | 142 | 44 | 125 | 139 | 106 | 59 | 92 | 2016-03-04 | 127 | 198 | 48 | 36 | 65 | 135 | 91 | 45 | 67
|  | 4 | 109 | 0.32059 | [5 empty] | agosto | 138 | 207 | 116 | 64 | 129 | 108 | 106 | 62 | 73 | 2016-03-05 | 101 | 168 | 69 | 41 | 68 | 100 | 91 | 29 | 83
|  | 5 | 85 | 0.25 | [5 empty] | set | 130 | 237 | 114 | 52 | 123 | 125 | 100 | 68 | 87 | 2016-03-06 | 109 | 172 | 89 | 35 | 45 | 87 | 92 | 33 | 69
|  | 6 | 82 | 0.24118 | [5 empty] | out | 126 | 256 | 118 | 53 | 118 | 120 | 98 | 97 | 110 | 2016-03-07 | 124 | 202 | 47 | 43 | 85 | 131 | 88 | 58 | 100
|  | 7 | 87 | 0.25588 | [5 empty] | nov | 136 | 269 | 138 | 69 | 120 | 137 | 104 | 79 | 88 | 2016-03-08 | 125 | 195 | 79 | 25 | 68 | 130 | 86 | 57 | 50
|  | 8 | 60 | 0.17647 | [5 empty] | dez | 137 | 259 | 103 | 48 | 127 | 143 | 102 | 66 | 87 | 2016-03-09 | 136 | 219 | 90 | 71 | 67 | 137 | 82 | 37 | 67
|  | 9 | 108 | 0.31765 | [15 empty] | 2016-03-10 | 120 | 208 | 48 | 59 | 93 | 124 | 90 | 53 | 74
|  | 10 | 120 | 0.35294 | [15 empty] | 2016-03-11 | 128 | 184 | 68 | 35 | 101 | 125 | 95 | 55 | 73
|  | 11 | 109 | 0.32059 |  |  |  |  | 2016 | jan | 140 | 229 | 110 | 85 | 128 | 141 | 107 | 70 | 90 | 2016-03-12 | 106 | 175 | 82 | 29 | 88 | 93 | 94 | 54 | 41
|  | 12 | 114 | 0.33529 | [5 empty] | fev | 143 | 238 | 132 | 91 | 124 | 149 | 100 | 69 | 102 | 2016-03-13 | 102 | 138 | 91 | 23 | 80 | 77 | 88 | 36 | 22
|  | 1 | 196.5755 | 0.57816 | [5 empty] | mar | 136 | 219 | 96 | 96 | 71 | 118 | 137 | 101 | 73 | 2016-03-14 | 129 | 201 | 82 | 22 | 113 | 122 | 92 | 58 | 50
|  | 2 | 161.4302 | 0.47479 | [5 empty] | abril | 133 | 196 | 109 | 79 | 109 | 134 | 109 | 70 | 92 | 2016-03-15 | 129 | 216 | 81 | 38 | 118 | 132 | 95 | 59 | 50
|  | 3 | 247.8042 | 0.72884 | [5 empty] | maio | 122 | 247 | 85 | 97 | 111 | 132 | 89 | 68 | 100 | 2016-03-16 | 130 | 200 | 84 | 48 | 109 | 128 | 100 | 53 | 40
|  | 4 | 231.7208 | 0.68153 | [5 empty] | jun | 128 | 242 | 82 | 66 | 108 | 125 | 106 | 71 | 83 | 2016-03-17 | 130 | 189 | 73 | 38 | 101 | 127 | 88 | 54 | 53
|  | 5 | 184.364 | 0.54225 | [5 empty] | jul | 153 | 255 | 87 | 52 | 117 | 130 | 111 | 82 | 151 | 2016-03-18 | 126 | 210 | 79 | 33 | 106 | 134 | 101 | 47 | 36
|  | 6 | 123.9021 | 0.36442 | [5 empty] | agosto | 143 | 200 | 60 | 52 | 111 | 126 | 107 | 61 | 83 | 2016-03-19 | 105 | 181 | 95 | 27 | 108 | 102 | 94 | 55 | 42
|  | 7 | 127.7741 | 0.37581 | [5 empty] | set | 152 | 228 | 108 | 78 | 120 | 127 | 115 | 56 | 87 | 2016-03-20 | 99 | 148 | 96 | 33 | 96 | 78 | 97 | 43 | 18
|  | 8 | 121.0726 | 0.3561 | [5 empty] | out | 131 | 243 | 120 | 60 | 113 | 126 | 109 | 67 | 110 | 2016-03-21 | 125 | 207 | 74 | 34 | 103 | 123 | 89 | 35 | 35
|  | 9 | 138.1985 | 0.40647 | [5 empty] | nov | 136 | 283 | 109 | 50 | 128 | 148 | 103 | 84 | 118 | 2016-03-22 | 114 | 205 | 71 | 27 | 72 | 124 | 83 | 54 | 48
|  | 10 | 150.2611 | 0.44194 | [5 empty] | dez | 149 | 254 | 114 | 84 | 122 | 150 | 110 | 91 | 108 | 2016-03-23 | 120 | 190 | 64 | 51 | 68 | 124 | 85 | 46 | 34
|  | 11 | 183.6194 | 0.54006 | [15 empty] | 2016-03-24 | 115 | 177 | 59 | 26 | 90 | 117 | 96 | 51 | 39
|  | 12 | 164.8553 | 0.48487 | [15 empty] | 2016-03-25 | 88 | 176 | 90 | 55 | 100 | 92 | 100 | 43 | 48
|  | 1 | 185.4064 | 0.54531 | [15 empty] | 2016-03-26 | 93 | 180 | 84 | 50 | 62 | 89 | 92 | 54 | 69
|  | 2 | 185.5553 | 0.54575 | [15 empty] | 2016-03-27 | 89 | 178 | 77 | 13 | 61 | 70 | 85 | 56 | 47
|  | 3 | 136.4115 | 0.40121 | [15 empty] | 2016-03-28 | 124 | 178 | 92 | 39 | 75 | 84 | 93 | 73 | 74
|  | 4 | 142.2194 | 0.41829 | [15 empty] | 2016-03-29 | 116 | 181 | 87 | 28 | 110 | 134 | 90 | 68 | 89
|  | 5 | 165.7489 | 0.4875 | [15 empty] | 2016-03-30 | 117 | 184 | 72 | 27 | 94 | 127 | 84 | 48 | 75
|  | 6 | 219.0625 | 0.6443 | [15 empty] | 2016-03-31 | 105 | 176 | 62 | 44 | 94 | 127 | 87 | 42 | 84 | 136 | 219 | 96 | 96 | 71 | 118 | 137 | 101 | 73
|  | 7 | 135.0712 | 0.39727 | [15 empty] | 2016-04-01 | 113 | 178 | 80 | 38 | 104 | 125 | 82 | 54 | 41
|  | 8 | 101.1172 | 0.2974 | [15 empty] | 2016-04-02 | 98 | 154 | 94 | 32 | 79 | 93 | 89 | 53 | 59
|  | 9 | 143.7086 | 0.42267 | [15 empty] | 2016-04-03 | 101 | 138 | 106 | 49 | 53 | 80 | 82 | 54 | 87
|  | 10 | 196.5755 | 0.57816 | [15 empty] | 2016-04-04 | 111 | 196 | 87 | 30 | 88 | 133 | 73 | 60 | 64
|  | 11 | 199.405 | 0.58649 | [15 empty] | 2016-04-05 | 109 | 178 | 80 | 22 | 91 | 126 | 82 | 40 | 48
|  | 12 | 228.13 | 0.67097 | [15 empty] | 2016-04-06 | 114 | 166 | 80 | 25 | 76 | 120 | 81 | 43 | 56
|  | 1 | 218.4668 | 0.64255 | [15 empty] | 2016-04-07 | 110 | 168 | 69 | 54 | 87 | 118 | 77 | 46 | 75
|  | 2 | 198.8093 | 0.58473 | [15 empty] | 2016-04-08 | 107 | 185 | 56 | 52 | 109 | 121 | 85 | 63 | 69
|  | 3 | 180.9388 | 0.53217 | [15 empty] | 2016-04-09 | 94 | 133 | 78 | 40 | 87 | 94 | 92 | 34 | 53
|  | 4 | 163.5151 | 0.48093 | [15 empty] | 2016-04-10 | 91 | 159 | 89 | 49 | 93 | 78 | 81 | 70 | 90
|  | 5 | 226.5086 | 0.6662 | [15 empty] | 2016-04-11 | 127 | 183 | 106 | 61 | 101 | 125 | 76 | 37 | 57
|  | 6 | 183.9172 | 0.54093 | [15 empty] | 2016-04-12 | 133 | 183 | 89 | 65 | 72 | 126 | 81 | 51 | 72
|  | 7 | 187.9381 | 0.55276 | [15 empty] | 2016-04-13 | 124 | 189 | 84 | 68 | 92 | 131 | 83 | 57 | 83
|  | 8 | 193.5971 | 0.5694 | [15 empty] | 2016-04-14 | 122 | 180 | 94 | 58 | 82 | 132 | 85 | 67 | 79
|  | 9 | 180.9388 | 0.53217 | [15 empty] | 2016-04-15 | 121 | 186 | 92 | 59 | 85 | 134 | 84 | 55 | 54
|  | 10 | 239.0179 | 0.70299 | [15 empty] | 2016-04-16 | 94 | 152 | 78 | 52 | 75 | 99 | 91 | 67 | 64
|  | 11 | 213.5525 | 0.6281 | [15 empty] | 2016-04-17 | 95 | 126 | 109 | 40 | 75 | 75 | 89 | 41 | 53
|  | 12 | 195.8309 | 0.57597 | [15 empty] | 2016-04-18 | 121 | 175 | 86 | 67 | 100 | 121 | 102 | 55 | 43
|  | 1 | 165.3 | 0.48618 | [15 empty] | 2016-04-19 | 120 | 195 | 63 | 30 | 65 | 128 | 90 | 59 | 70
|  | 2 | 161.8769 | 0.47611 | [15 empty] | 2016-04-20 | 118 | 182 | 68 | 61 | 86 | 120 | 102 | 38 | 68
|  | 3 | 187.6402 | 0.55188 | [15 empty] | 2016-04-21 | 116 | 174 | 76 | 68 | 105 | 123 | 108 | 48 | 72
|  | 4 | 192.5546 | 0.56634 | [15 empty] | 2016-04-22 | 121 | 164 | 58 | 47 | 105 | 119 | 109 | 49 | 27
|  | 5 | 209.6805 | 0.61671 | [15 empty] | 2016-04-23 | 86 | 116 | 41 | 51 | 78 | 86 | 102 | 37 | 31
|  | 6 | 249.2935 | 0.73322 | [15 empty] | 2016-04-24 | 80 | 101 | 47 | 43 | 67 | 63 | 98 | 35 | 33
|  | 7 | 177.5136 | 0.5221 | [15 empty] | 2016-04-25 | 86 | 103 | 43 | 79 | 76 | 67 | 97 | 39 | 35
|  | 8 | 155.3244 | 0.45684 | [15 empty] | 2016-04-26 | 107 | 135 | 29 | 48 | 98 | 112 | 97 | 45 | 25
|  | 9 | 170.8122 | 0.50239 | [15 empty] | 2016-04-27 | 111 | 146 | 41 | 53 | 76 | 118 | 89 | 48 | 32
|  | 10 | 183.9172 | 0.54093 | [15 empty] | 2016-04-28 | 115 | 140 | 45 | 24 | 91 | 114 | 92 | 44 | 23
|  | 11 | 269.3978 | 0.79235 | [15 empty] | 2016-04-29 | 112 | 142 | 38 | 25 | 104 | 114 | 95 | 52 | 69
|  | 12 | 246.1661 | 0.72402 | [15 empty] | 2016-04-30 | 83 | 128 | 18 | 42 | 104 | 83 | 82 | 36 | 92 | 133 | 196 | 109 | 79 | 109 | 134 | 109 | 70 | 92
|  | 1 | 215.6373 | 0.63423 | [15 empty] | 2016-05-01 | 90 | 106 | 52 | 54 | 65 | 62 | 70 | 55 | 60
|  | 2 | 239.1668 | 0.70343 | [15 empty] | 2016-05-02 | 107 | 151 | 35 | 75 | 97 | 112 | 85 | 41 | 28
|  | 3 | 251.3783 | 0.73935 | [15 empty] | 2016-05-03 | 113 | 144 | 46 | 82 | 77 | 114 | 87 | 43 | 29
|  | 4 | 205.3618 | 0.60401 | [15 empty] | 2016-05-04 | 115 | 152 | 44 | 61 | 100 | 115 | 84 | 45 | 33
|  | 5 | 176.3223 | 0.51859 | [15 empty] | 2016-05-05 | 98 | 171 | 45 | 59 | 105 | 118 | 87 | 50 | 48
|  | 6 | 176.4712 | 0.51903 | [15 empty] | 2016-05-06 | 113 | 167 | 39 | 50 | 85 | 120 | 84 | 44 | 33
|  | 7 | 178.8539 | 0.52604 | [15 empty] | 2016-05-07 | 93 | 137 | 37 | 61 | 78 | 88 | 80 | 58 | 71
|  | 8 | 165.8978 | 0.48793 | [15 empty] | 2016-05-08 | 88 | 116 | 43 | 95 | 101 | 69 | 77 | 68 | 100
|  | 9 | 213.8503 | 0.62897 | [15 empty] | 2016-05-09 | 116 | 158 | 40 | 86 | 81 | 118 | 72 | 63 | 83
|  | 10 | 170.6633 | 0.50195 | [15 empty] | 2016-05-10 | 114 | 161 | 47 | 97 | 86 | 132 | 74 | 53 | 54
|  | 11 | 228.5935 | 0.67233 | [15 empty] | 2016-05-11 | 118 | 165 | 54 | 83 | 100 | 121 | 72 | 41 | 66
|  | 12 | 242.7409 | 0.71394 | [15 empty] | 2016-05-12 | 117 | 161 | 63 | 75 | 102 | 118 | 76 | 52 | 69
|  | 1 | 185 | 0.54412 | [15 empty] | 2016-05-13 | 118 | 157 | 52 | 89 | 66 | 124 | 77 | 31 | 72
|  | 2 | 196 | 0.57647 | [15 empty] | 2016-05-14 | 89 | 123 | 64 | 91 | 49 | 92 | 80 | 33 | 46
|  | 3 | 199 | 0.58529 | [15 empty] | 2016-05-15 | 84 | 113 | 49 | 73 | 61 | 68 | 77 | 36 | 41
|  | 4 | 168 | 0.49412 | [15 empty] | 2016-05-16 | 109 | 142 | 63 | 68 | 94 | 115 | 85 | 44 | 59
|  | 5 | 192 | 0.56471 | [15 empty] | 2016-05-17 | 122 | 143 | 45 | 64 | 56 | 118 | 76 | 47 | 69
|  | 6 | 199 | 0.58529 | [15 empty] | 2016-05-18 | 113 | 140 | 38 | 61 | 90 | 120 | 84 | 43 | 55
|  | 7 | 150 | 0.44118 | [15 empty] | 2016-05-19 | 106 | 169 | 42 | 63 | 83 | 116 | 83 | 41 | 63
|  | 8 | 169 | 0.49706 | [15 empty] | 2016-05-20 | 118 | 164 | 81 | 64 | 111 | 115 | 89 | 44 | 71
|  | 9 | 186 | 0.54706 | [15 empty] | 2016-05-21 | 92 | 109 | 85 | 39 | 71 | 84 | 86 | 30 | 50
|  | 10 | 211 | 0.62059 | [15 empty] | 2016-05-22 | 85 | 128 | 77 | 39 | 85 | 63 | 80 | 42 | 38
|  | 11 | 169 | 0.49706 | [15 empty] | 2016-05-23 | 109 | 195 | 74 | 55 | 100 | 111 | 76 | 41 | 68
|  | 12 | 193 | 0.56765 | [15 empty] | 2016-05-24 | 119 | 169 | 73 | 46 | 86 | 120 | 76 | 40 | 30
|  | 1 | 216 | 0.63529 | [15 empty] | 2016-05-25 | 114 | 247 | 59 | 37 | 95 | 117 | 81 | 37 | 51
|  | 2 | 222 | 0.65294 | [15 empty] | 2016-05-26 | 88 | 128 | 74 | 41 | 70 | 68 | 88 | 37 | 46
|  | 3 | 150 | 0.44118 | [15 empty] | 2016-05-27 | 112 | 147 | 53 | 51 | 74 | 95 | 84 | 29 | 70
|  | 4 | 206 | 0.60588 | [15 empty] | 2016-05-28 | 83 | 125 | 69 | 56 | 60 | 83 | 79 | 52 | 80
|  | 5 | 190 | 0.55882 | [15 empty] | 2016-05-29 | 81 | 133 | 63 | 29 | 54 | 64 | 83 | 61 | 80
|  | 6 | 159 | 0.46765 | [15 empty] | 2016-05-30 | 106 | 161 | 55 | 49 | 64 | 111 | 76 | 40 | 29
|  | 7 | 174 | 0.51176 | [15 empty] | 2016-05-31 | 113 | 171 | 51 | 49 | 66 | 113 | 81 | 23 | 33 | 122 | 247 | 85 | 97 | 111 | 132 | 89 | 68 | 100
|  | 8 | 172 | 0.50588 | [15 empty] | 2016-06-01 | 115 | 168 | 57 | 17 | 90 | 114 | 83 | 22 | 41
|  | 9 | 188 | 0.55294 | [15 empty] | 2016-06-02 | 115 | 176 | 57 | 54 | 95 | 115 | 87 | 20 | 49
|  | 10 | 165 | 0.48529 | [15 empty] | 2016-06-03 | 112 | 163 | 78 | 42 | 95 | 116 | 87 | 22 | 31
|  | 11 | 211 | 0.62059 | [15 empty] | 2016-06-04 | 88 | 126 | 75 | 43 | 74 | 82 | 87 | 19 | 29
|  | 12 | 220 | 0.64706 | [15 empty] | 2016-06-05 | 86 | 137 | 82 | 66 | 60 | 63 | 88 | 18 | 23
|  | 1 | 204 | 0.6 | [15 empty] | 2016-06-06 | 118 | 213 | 64 | 18 | 95 | 113 | 84 | 20 | 31
|  | 2 | 239 | 0.70294 | [15 empty] | 2016-06-07 | 120 | 207 | 54 | 17 | 102 | 114 | 82 | 21 | 41
|  | 3 | 153 | 0.45 | [15 empty] | 2016-06-08 | 126 | 211 | 45 | 19 | 97 | 117 | 96 | 25 | 83
|  | 4 | 148 | 0.43529 | [15 empty] | 2016-06-09 | 113 | 201 | 24 | 59 | 67 | 118 | 95 | 24 | 39
|  | 5 | 189 | 0.55588 | [15 empty] | 2016-06-10 | 87 | 144 | 47 | 65 | 90 | 72 | 90 | 18 | 40
|  | 6 | 210 | 0.61765 | [15 empty] | 2016-06-11 | 86 | 147 | 28 | 48 | 81 | 67 | 90 | 35 | 29
|  | 7 | 193 | 0.56765 | [15 empty] | 2016-06-12 | 84 | 157 | 32 | 57 | 54 | 65 | 90 | 20 | 18
|  | 8 | 123 | 0.36176 | [15 empty] | 2016-06-13 | 106 | 200 | 29 | 52 | 71 | 121 | 89 | 36 | 27
|  | 9 | 186 | 0.54706 | [15 empty] | 2016-06-14 | 113 | 200 | 45 | 50 | 89 | 124 | 89 | 57 | 38
|  | 10 | 189 | 0.55588 | [15 empty] | 2016-06-15 | 110 | 204 | 32 | 56 | 66 | 122 | 92 | 71 | 56
|  | 11 | 182 | 0.53529 | [15 empty] | 2016-06-16 | 110 | 195 | 48 | 49 | 77 | 122 | 91 | 34 | 32
|  | 12 | 193 | 0.56765 | [15 empty] | 2016-06-17 | 112 | 197 | 35 | 54 | 95 | 118 | 88 | 19 | 29
|  | 1 | 199 | 0.58529 | [15 empty] | 2016-06-18 | 91 | 169 | 24 | 45 | 99 | 83 | 90 | 30 | 62
|  | 2 | 179 | 0.52647 | [15 empty] | 2016-06-19 | 89 | 163 | 37 | 33 | 95 | 64 | 90 | 17 | 65
|  | 3 | 141 | 0.41471 | [15 empty] | 2016-06-20 | 123 | 205 | 39 | 30 | 92 | 117 | 89 | 24 | 38
|  | 4 | 136 | 0.4 | [15 empty] | 2016-06-21 | 125 | 204 | 50 | 20 | 106 | 121 | 84 | 23 | 55
|  | 5 | 168 | 0.49412 | [15 empty] | 2016-06-22 | 126 | 242 | 49 | 26 | 106 | 125 | 96 | 24 | 51
|  | 6 | 139 | 0.40882 | [15 empty] | 2016-06-23 | 128 | 214 | 49 | 26 | 108 | 121 | 90 | 24 | 48
|  | 7 | 113 | 0.33235 | [15 empty] | 2016-06-24 | 115 | 181 | 24 | 34 | 77 | 100 | 91 | 24 | 35
|  | 8 | 67 | 0.19706 | [15 empty] | 2016-06-25 | 86 | 152 | 30 | 32 | 103 | 81 | 101 | 18 | 41
|  | 9 | 171 | 0.50294 | [15 empty] | 2016-06-26 | 88 | 146 | 49 | 40 | 79 | 68 | 106 | 66 | 44
|  | 10 | 150 | 0.44118 | [15 empty] | 2016-06-27 | 125 | 207 | 53 | 57 | 101 | 119 | 95 | 58 | 70
|  | 11 | 195 | 0.57353 | [15 empty] | 2016-06-28 | 121 | 205 | 40 | 34 | 80 | 123 | 95 | 29 | 48
|  | 12 | 226 | 0.66471 | [15 empty] | 2016-06-29 | 111 | 208 | 48 | 38 | 87 | 124 | 103 | 29 | 45
|  | 1 |  | 0 | [15 empty] | 2016-06-30 | 114 | 200 | 39 | 40 | 79 | 119 | 96 | 30 | 73 | 128 | 242 | 82 | 66 | 108 | 125 | 106 | 71 | 83
|  | 2 |  | 0 | [15 empty] | 2016-07-01 | 110 | 200 | 45 | 32 | 80 | 120 | 89 | 29 | 68
|  | 3 |  | 0 | [15 empty] | 2016-07-02 | 85 | 162 | 33 | 29 | 106 | 89 | 92 | 25 | 62
|  | 4 |  | 0 | [15 empty] | 2016-07-03 | 90 | 157 | 56 | 23 | 78 | 72 | 86 | 58 | 54
|  | 5 |  | 0 | [15 empty] | 2016-07-04 | 110 | 207 | 87 | 32 | 105 | 112 | 98 | 29 | 51
|  | 6 |  | 0 | [15 empty] | 2016-07-05 | 119 | 212 | 75 | 28 | 107 | 122 | 93 | 31 | 80
|  | 7 |  | 0 | [15 empty] | 2016-07-06 | 110 | 216 | 60 | 43 | 106 | 129 | 101 | 37 | 59
|  | 8 |  | 0 | [15 empty] | 2016-07-07 | 112 | 215 | 56 | 30 | 107 | 130 | 92 | 31 | 47
|  | 9 |  | 0 | [15 empty] | 2016-07-08 | 110 | 172 | 42 | 28 | 78 | 123 | 96 | 48 | 46
|  | 10 |  | 0 | [15 empty] | 2016-07-09 | 97 | 155 | 34 | 34 | 87 | 88 | 93 | 48 | 35
|  | 11 |  | 0 | [15 empty] | 2016-07-10 | 81 | 156 | 25 | 44 | 117 | 67 | 90 | 33 | 46
|  | 12 |  | 0 | [15 empty] | 2016-07-11 | 114 | 203 | 19 | 52 | 89 | 116 | 95 | 49 | 49
|  | 1 |  | 0 | [15 empty] | 2016-07-12 | 105 | 214 | 26 | 37 | 89 | 116 | 90 | 44 | 58
|  | 2 |  | 0 | [15 empty] | 2016-07-13 | 125 | 234 | 20 | 38 | 78 | 119 | 88 | 48 | 70
|  | 3 |  | 0 | [15 empty] | 2016-07-14 | 138 | 211 | 40 | 31 | 104 | 122 | 100 | 54 | 53
|  | 4 |  | 0 | [15 empty] | 2016-07-15 | 135 | 213 | 51 | 34 | 117 | 124 | 103 | 56 | 59
|  | 5 |  | 0 | [15 empty] | 2016-07-16 | 101 | 174 | 47 | 19 | 96 | 89 | 99 | 48 | 43
|  | 6 |  | 0 | [15 empty] | 2016-07-17 | 96 | 159 | 59 | 20 | 79 | 74 | 96 | 46 | 33
|  | 7 |  | 0 | [15 empty] | 2016-07-18 | 131 | 239 | 67 | 23 | 104 | 119 | 101 | 55 | 50
|  | 8 |  | 0 | [15 empty] | 2016-07-19 | 138 | 208 | 61 | 31 | 112 | 125 | 106 | 56 | 48
|  | 9 |  | 0 | [15 empty] | 2016-07-20 | 130 | 205 | 27 | 41 | 50 | 123 | 111 | 56 | 39
|  | 10 |  | 0 | [15 empty] | 2016-07-21 | 119 | 241 | 16 | 48 | 58 | 124 | 101 | 50 | 48
|  | 11 |  | 0 | [15 empty] | 2016-07-22 | 114 | 255 | 21 | 27 | 67 | 124 | 96 | 50 | 42
|  | 12 |  | 0 | [15 empty] | 2016-07-23 | 95 | 174 | 21 | 19 | 90 | 91 | 101 | 43 | 69
[20 empty] | 2016-07-24 | 95 | 147 | 34 | 23 | 82 | 74 | 97 | 46 | 49
[20 empty] | 2016-07-25 | 138 | 212 | 35 | 25 | 114 | 126 | 103 | 77 | 134
[20 empty] | 2016-07-26 | 129 | 209 | 21 | 33 | 53 | 127 | 101 | 82 | 124
[20 empty] | 2016-07-27 | 145 | 203 | 35 | 21 | 107 | 126 | 103 | 58 | 151
[20 empty] | 2016-07-28 | 153 | 208 | 56 | 23 | 113 | 128 | 104 | 60 | 125
[20 empty] | 2016-07-29 | 143 | 196 | 57 | 30 | 114 | 126 | 102 | 61 | 98
[20 empty] | 2016-07-30 | 98 | 161 | 56 | 43 | 100 | 83 | 102 | 46 | 32
[20 empty] | 2016-07-31 | 82 | 150 | 33 | 26 | 63 | 66 | 87 | 41 | 30 | 153 | 255 | 87 | 52 | 117 | 130 | 111 | 82 | 151
[20 empty] | 2016-08-01 | 124 | 195 | 18 | 28 | 74 | 109 | 102 | 51 | 39
[20 empty] | 2016-08-02 | 124 | 199 | 46 | 31 | 100 | 114 | 103 | 55 | 56
[20 empty] | 2016-08-03 | 108 | 198 | 33 | 41 | 87 | 126 | 102 | 53 | 63
[20 empty] | 2016-08-04 | 113 | 199 | 34 | 51 | 53 | 113 | 95 | 48 | 37
[20 empty] | 2016-08-05 | 113 | 191 | 27 | 37 | 56 | 111 | 102 | 53 | 74
[20 empty] | 2016-08-06 | 101 | 162 | 52 | 26 | 93 | 81 | 105 | 41 | 41
[20 empty] | 2016-08-07 | 100 | 138 | 59 | 26 | 80 | 70 | 95 | 55 | 39
[20 empty] | 2016-08-08 | 135 | 191 | 59 | 37 | 102 | 113 | 95 | 59 | 70
[20 empty] | 2016-08-09 | 126 | 178 | 39 | 26 | 52 | 115 | 99 | 61 | 77
[20 empty] | 2016-08-10 | 136 | 176 | 58 | 40 | 101 | 108 | 93 | 58 | 48
[20 empty] | 2016-08-11 | 134 | 182 | 57 | 39 | 111 | 108 | 93 | 54 | 69
[20 empty] | 2016-08-12 | 138 | 165 | 57 | 29 | 108 | 105 | 96 | 57 | 44
[20 empty] | 2016-08-13 | 104 | 163 | 46 | 25 | 76 | 76 | 97 | 45 | 42
[20 empty] | 2016-08-14 | 97 | 145 | 59 | 22 | 95 | 72 | 106 | 41 | 45
[20 empty] | 2016-08-15 | 100 | 155 | 55 | 36 | 81 | 65 | 95 | 36 | 36
[20 empty] | 2016-08-16 | 129 | 174 | 53 | 42 | 71 | 82 | 97 | 42 | 48
[20 empty] | 2016-08-17 | 132 | 171 | 50 | 16 | 102 | 85 | 93 | 44 | 59
[20 empty] | 2016-08-18 | 129 | 147 | 38 | 34 | 72 | 82 | 90 | 47 | 68
[20 empty] | 2016-08-19 | 143 | 171 | 60 | 24 | 101 | 84 | 90 | 42 | 78
[20 empty] | 2016-08-20 | 95 | 151 | 21 | 26 | 86 | 68 | 89 | 43 | 83
[20 empty] | 2016-08-21 | 99 | 148 | 36 | 21 | 86 | 65 | 94 | 37 | 81
[20 empty] | 2016-08-22 | 136 | 172 | 45 | 38 | 106 | 83 | 93 | 46 | 50
[20 empty] | 2016-08-23 | 142 | 181 | 43 | 31 | 96 | 86 | 98 | 48 | 32
[20 empty] | 2016-08-24 | 137 | 196 | 42 | 32 | 90 | 85 | 106 | 46 | 41
[20 empty] | 2016-08-25 | 128 | 197 | 37 | 30 | 72 | 84 | 101 | 47 | 52
[20 empty] | 2016-08-26 | 141 | 187 | 43 | 51 | 101 | 88 | 107 | 50 | 22
[20 empty] | 2016-08-27 | 107 | 136 | 41 | 28 | 89 | 71 | 101 | 41 | 60
[20 empty] | 2016-08-28 | 94 | 152 | 30 | 52 | 103 | 68 | 90 | 40 | 68
[20 empty] | 2016-08-29 | 137 | 170 | 24 | 28 | 95 | 93 | 104 | 55 | 78
[20 empty] | 2016-08-30 | 130 | 200 | 21 | 42 | 90 | 96 | 92 | 56 | 50
[20 empty] | 2016-08-31 | 128 | 198 | 20 | 33 | 66 | 96 | 95 | 57 | 45 | 143 | 200 | 60 | 52 | 111 | 126 | 107 | 61 | 83
[20 empty] | 2016-09-01 | 141 | 199 | 44 | 38 | 112 | 103 | 90 | 56 | 60
[20 empty] | 2016-09-02 | 143 | 180 | 62 | 26 | 110 | 104 | 94 | 50 | 18
[20 empty] | 2016-09-03 | 112 | 161 | 47 | 31 | 95 | 76 | 92 | 47 | 21
[20 empty] | 2016-09-04 | 109 | 162 | 60 | 28 | 83 | 69 | 93 | 42 | 24
[20 empty] | 2016-09-05 | 149 | 207 | 52 | 49 | 105 | 121 | 90 | 56 | 23
[20 empty] | 2016-09-06 | 152 | 186 | 89 | 35 | 120 | 127 | 97 | 50 | 18
[20 empty] | 2016-09-07 | 129 | 216 | 69 | 31 | 109 | 121 | 93 | 49 | 53
[20 empty] | 2016-09-08 | 121 | 206 | 23 | 19 | 74 | 120 | 91 | 50 | 60
[20 empty] | 2016-09-09 | 124 | 194 | 19 | 46 | 67 | 117 | 93 | 50 | 57
[20 empty] | 2016-09-10 | 97 | 161 | 21 | 31 | 51 | 83 | 91 | 45 | 25
[20 empty] | 2016-09-11 | 103 | 164 | 54 | 36 | 73 | 69 | 91 | 43 | 29
[20 empty] | 2016-09-12 | 138 | 201 | 72 | 44 | 114 | 117 | 106 | 43 | 52
[20 empty] | 2016-09-13 | 138 | 216 | 50 | 78 | 62 | 120 | 94 | 32 | 81
[20 empty] | 2016-09-14 | 133 | 214 | 52 | 59 | 101 | 116 | 102 | 41 | 37
[20 empty] | 2016-09-15 | 134 | 215 | 66 | 19 | 109 | 120 | 105 | 44 | 39
[20 empty] | 2016-09-16 | 124 | 207 | 40 | 37 | 72 | 117 | 100 | 49 | 63
[20 empty] | 2016-09-17 | 102 | 180 | 43 | 28 | 93 | 86 | 100 | 42 | 69
[20 empty] | 2016-09-18 | 104 | 162 | 51 | 40 | 84 | 68 | 99 | 39 | 40
[20 empty] | 2016-09-19 | 131 | 199 | 51 | 27 | 113 | 117 | 104 | 51 | 39
[20 empty] | 2016-09-20 | 130 | 203 | 50 | 22 | 105 | 117 | 108 | 53 | 17
[20 empty] | 2016-09-21 | 123 | 209 | 49 | 23 | 77 | 122 | 112 | 53 | 21
[20 empty] | 2016-09-22 | 124 | 200 | 70 | 27 | 71 | 121 | 107 | 52 | 41
[20 empty] | 2016-09-23 | 127 | 199 | 52 | 23 | 98 | 117 | 115 | 53 | 27
[20 empty] | 2016-09-24 | 103 | 171 | 108 | 21 | 93 | 85 | 105 | 36 | 75
[20 empty] | 2016-09-25 | 95 | 165 | 93 | 28 | 69 | 69 | 98 | 41 | 56
[20 empty] | 2016-09-26 | 115 | 227 | 34 | 33 | 85 | 115 | 102 | 50 | 50
[20 empty] | 2016-09-27 | 133 | 226 | 55 | 42 | 97 | 118 | 112 | 47 | 87
[20 empty] | 2016-09-28 | 141 | 217 | 66 | 57 | 96 | 119 | 100 | 48 | 31
[20 empty] | 2016-09-29 | 140 | 228 | 54 | 53 | 113 | 118 | 100 | 54 | 49
[20 empty] | 2016-09-30 | 136 | 212 | 56 | 30 | 115 | 117 | 103 | 48 | 42 | 152 | 228 | 108 | 78 | 120 | 127 | 115 | 56 | 87
[20 empty] | 2016-10-01 | 104 | 168 | 50 | 23 | 77 | 82 | 100 | 43 | 83
[20 empty] | 2016-10-02 | 102 | 161 | 75 | 29 | 57 | 67 | 94 | 41 | 44
[20 empty] | 2016-10-03 | 131 | 201 | 75 | 26 | 105 | 112 | 100 | 51 | 26
[20 empty] | 2016-10-04 | 123 | 216 | 57 | 25 | 87 | 110 | 98 | 50 | 60
[20 empty] | 2016-10-05 | 107 | 165 | 90 | 27 | 84 | 75 | 98 | 48 | 61
[20 empty] | 2016-10-06 | 129 | 197 | 67 | 19 | 110 | 110 | 102 | 55 | 26
[20 empty] | 2016-10-07 | 126 | 199 | 68 | 21 | 99 | 113 | 95 | 54 | 35
[20 empty] | 2016-10-08 | 93 | 165 | 56 | 24 | 69 | 86 | 92 | 47 | 71
[20 empty] | 2016-10-09 | 98 | 162 | 80 | 28 | 64 | 69 | 85 | 43 | 29
[20 empty] | 2016-10-10 | 123 | 230 | 67 | 23 | 111 | 116 | 99 | 53 | 33
[20 empty] | 2016-10-11 | 120 | 204 | 64 | 22 | 100 | 119 | 107 | 42 | 70
[20 empty] | 2016-10-12 | 121 | 199 | 87 | 26 | 113 | 118 | 107 | 57 | 47
[20 empty] | 2016-10-13 | 124 | 215 | 68 | 21 | 100 | 124 | 103 | 49 | 55
[20 empty] | 2016-10-14 | 117 | 207 | 67 | 33 | 98 | 118 | 93 | 47 | 66
[20 empty] | 2016-10-15 | 104 | 194 | 67 | 28 | 73 | 93 | 100 | 50 | 92
[20 empty] | 2016-10-16 | 100 | 173 | 88 | 26 | 92 | 71 | 89 | 53 | 76
[20 empty] | 2016-10-17 | 119 | 214 | 95 | 16 | 94 | 118 | 97 | 49 | 54
[20 empty] | 2016-10-18 | 126 | 214 | 75 | 12 | 113 | 126 | 101 | 49 | 36
[20 empty] | 2016-10-19 | 121 | 243 | 73 | 12 | 112 | 124 | 94 | 53 | 19
[20 empty] | 2016-10-20 | 125 | 209 | 91 | 19 | 113 | 121 | 92 | 53 | 18
[20 empty] | 2016-10-21 | 119 | 203 | 88 | 33 | 109 | 120 | 95 | 52 | 51
[20 empty] | 2016-10-22 | 90 | 176 | 65 | 48 | 80 | 92 | 87 | 56 | 61
[20 empty] | 2016-10-23 | 93 | 172 | 72 | 25 | 48 | 70 | 81 | 60 | 83
[20 empty] | 2016-10-24 | 120 | 191 | 59 | 60 | 93 | 119 | 81 | 55 | 92
[20 empty] | 2016-10-25 | 118 | 203 | 114 | 52 | 98 | 120 | 81 | 64 | 76
[20 empty] | 2016-10-26 | 125 | 189 | 120 | 49 | 103 | 121 | 95 | 49 | 110
[20 empty] | 2016-10-27 | 120 | 220 | 86 | 50 | 85 | 120 | 109 | 51 | 81
[20 empty] | 2016-10-28 | 120 | 202 | 83 | 49 | 109 | 119 | 101 | 52 | 99
[20 empty] | 2016-10-29 | 100 | 176 | 92 | 53 | 77 | 89 | 97 | 48 | 36
[20 empty] | 2016-10-30 | 93 | 151 | 107 | 23 | 85 | 68 | 91 | 41 | 26
[20 empty] | 2016-10-31 | 120 | 186 | 86 | 35 | 86 | 100 | 80 | 67 | 38 | 131 | 243 | 120 | 60 | 113 | 126 | 109 | 67 | 110
[20 empty] | 2016-11-01 | 102 | 161 | 93 | 20 | 85 | 70 | 96 | 36 | 62
[20 empty] | 2016-11-02 | 125 | 200 | 102 | 22 | 106 | 122 | 88 | 74 | 53
[20 empty] | 2016-11-03 | 123 | 213 | 103 | 23 | 100 | 123 | 88 | 74 | 52
[20 empty] | 2016-11-04 | 121 | 209 | 74 | 27 | 113 | 119 | 89 | 62 | 51
[20 empty] | 2016-11-05 | 93 | 188 | 60 | 30 | 71 | 82 | 88 | 24 | 71
[20 empty] | 2016-11-06 | 93 | 167 | 91 | 32 | 50 | 70 | 88 | 41 | 60
[20 empty] | 2016-11-07 | 121 | 226 | 74 | 28 | 52 | 126 | 82 | 79 | 65
[20 empty] | 2016-11-08 | 125 | 226 | 91 | 33 | 109 | 134 | 98 | 84 | 77
[20 empty] | 2016-11-09 | 131 | 209 | 92 | 28 | 106 | 132 | 95 | 83 | 74
[20 empty] | 2016-11-10 | 127 | 226 | 91 | 23 | 113 | 133 | 92 | 61 | 80
[20 empty] | 2016-11-11 | 131 | 240 | 79 | 26 | 116 | 127 | 100 | 54 | 118
[20 empty] | 2016-11-12 | 100 | 189 | 80 | 26 | 100 | 98 | 94 | 54 | 43
[20 empty] | 2016-11-13 | 99 | 172 | 108 | 19 | 84 | 76 | 89 | 39 | 61
[20 empty] | 2016-11-14 | 122 | 230 | 80 | 47 | 111 | 130 | 87 | 60 | 53
[20 empty] | 2016-11-15 | 125 | 233 | 84 | 39 | 104 | 133 | 85 | 59 | 58
[20 empty] | 2016-11-16 | 133 | 231 | 99 | 24 | 108 | 132 | 87 | 60 | 59
[20 empty] | 2016-11-17 | 134 | 223 | 94 | 32 | 109 | 134 | 99 | 58 | 59
[20 empty] | 2016-11-18 | 128 | 220 | 101 | 24 | 107 | 129 | 96 | 48 | 51
[20 empty] | 2016-11-19 | 105 | 207 | 75 | 25 | 87 | 96 | 91 | 42 | 55
[20 empty] | 2016-11-20 | 94 | 193 | 70 | 24 | 94 | 80 | 86 | 62 | 80
[20 empty] | 2016-11-21 | 133 | 232 | 87 | 35 | 122 | 131 | 89 | 66 | 88
[20 empty] | 2016-11-22 | 132 | 245 | 77 | 25 | 108 | 137 | 93 | 58 | 46
[20 empty] | 2016-11-23 | 124 | 207 | 67 | 24 | 90 | 137 | 103 | 62 | 67
[20 empty] | 2016-11-24 | 136 | 259 | 76 | 26 | 109 | 148 | 103 | 56 | 51
[20 empty] | 2016-11-25 | 134 | 238 | 87 | 34 | 120 | 142 | 100 | 36 | 74
[20 empty] | 2016-11-26 | 110 | 205 | 90 | 17 | 72 | 112 | 98 | 40 | 47
[20 empty] | 2016-11-27 | 107 | 194 | 109 | 23 | 77 | 89 | 94 | 43 | 44
[20 empty] | 2016-11-28 | 135 | 239 | 91 | 23 | 128 | 141 | 93 | 68 | 69
[20 empty] | 2016-11-29 | 134 | 283 | 85 | 43 | 81 | 147 | 97 | 53 | 77
[20 empty] | 2016-11-30 | 129 | 260 | 84 | 50 | 101 | 148 | 88 | 55 | 40 | 136 | 283 | 109 | 50 | 128 | 148 | 103 | 84 | 118
[20 empty] | 2016-12-01 | 111 | 187 | 99 | 43 | 84 | 96 | 100 | 53 | 51
[20 empty] | 2016-12-02 | 134 | 216 | 68 | 25 | 66 | 124 | 89 | 63 | 68
[20 empty] | 2016-12-03 | 111 | 190 | 85 | 46 | 103 | 100 | 85 | 46 | 49
[20 empty] | 2016-12-04 | 105 | 178 | 79 | 46 | 96 | 86 | 78 | 45 | 28
[20 empty] | 2016-12-05 | 126 | 226 | 86 | 84 | 118 | 137 | 89 | 59 | 75
[20 empty] | 2016-12-06 | 134 | 227 | 88 | 80 | 110 | 134 | 90 | 56 | 50
[20 empty] | 2016-12-07 | 136 | 208 | 81 | 36 | 63 | 137 | 98 | 57 | 48
[20 empty] | 2016-12-08 | 104 | 211 | 55 | 48 | 98 | 85 | 84 | 34 | 54
[20 empty] | 2016-12-09 | 124 | 209 | 48 | 43 | 98 | 117 | 96 | 23 | 72
[20 empty] | 2016-12-10 | 101 | 185 | 71 | 35 | 49 | 94 | 100 | 50 | 77
[20 empty] | 2016-12-11 | 103 | 181 | 73 | 37 | 93 | 84 | 95 | 50 | 54
[20 empty] | 2016-12-12 | 138 | 230 | 96 | 25 | 118 | 140 | 110 | 63 | 97
[20 empty] | 2016-12-13 | 149 | 233 | 97 | 35 | 99 | 142 | 106 | 82 | 58
[20 empty] | 2016-12-14 | 125 | 240 | 79 | 39 | 86 | 144 | 98 | 82 | 63
[20 empty] | 2016-12-15 | 133 | 242 | 105 | 48 | 115 | 149 | 97 | 61 | 67
[20 empty] | 2016-12-16 | 123 | 250 | 65 | 46 | 87 | 143 | 98 | 42 | 67
[20 empty] | 2016-12-17 | 112 | 203 | 84 | 35 | 62 | 99 | 96 | 55 | 48
[20 empty] | 2016-12-18 | 102 | 190 | 92 | 74 | 98 | 86 | 91 | 51 | 50
[20 empty] | 2016-12-19 | 131 | 254 | 85 | 35 | 87 | 144 | 101 | 59 | 53
[20 empty] | 2016-12-20 | 142 | 250 | 90 | 39 | 100 | 150 | 107 | 91 | 51
[20 empty] | 2016-12-21 | 133 | 238 | 101 | 46 | 114 | 149 | 100 | 74 | 78
[20 empty] | 2016-12-22 | 137 | 229 | 96 | 34 | 117 | 139 | 105 | 71 | 74
[20 empty] | 2016-12-23 | 125 | 204 | 83 | 23 | 104 | 130 | 103 | 66 | 61
[20 empty] | 2016-12-24 | 101 | 180 | 94 | 37 | 86 | 92 | 85 | 52 | 48
[20 empty] | 2016-12-25 | 90 | 187 | 96 | 32 | 84 | 81 | 85 | 52 | 36
[20 empty] | 2016-12-26 | 132 | 225 | 110 | 32 | 122 | 98 | 94 | 53 | 63
[20 empty] | 2016-12-27 | 122 | 215 | 90 | 48 | 121 | 116 | 103 | 68 | 87
[20 empty] | 2016-12-28 | 123 | 214 | 114 | 23 | 80 | 118 | 88 | 62 | 95
[20 empty] | 2016-12-29 | 123 | 208 | 95 | 39 | 114 | 117 | 99 | 61 | 108
[20 empty] | 2016-12-30 | 121 | 224 | 90 | 33 | 114 | 112 | 106 | 72 | 108
[20 empty] | 2016-12-31 | 101 | 221 | 106 | 36 | 99 | 104 | 96 | 72 | 74 | 149 | 254 | 114 | 84 | 122 | 150 | 110 | 91 | 108
[20 empty] | 2017-01-01 | 104 | 198 | 91 | 28 | 48 | 85 | 88 | 56 | 57

## Maintenance
Maintenance
Rating Code | Bushings | Oil leaks | Oil level | Infra-red | Cooling | Main Tank | Oil tank | Foundation | Grounding | Gaskets | Connectors
A | 0 | 0-2 | 0 | 0 | 0-3 | 0 | 0 | 0 | 0 | 0 | 0
B | 1-2 | 3-4 | 1-2 | 1 | 4-6 | 1-2 | 1-2 | 1-2 | 1-2 | 1-2 | 1-2
C | 3-4 | 5-6 | 3-4 | 2-3 | 7-10 | 3-4 | 3-4 | 3-4 | 3 | 3-4 | 3
D | 5-7 | 7-8 | 5-6 | 4-5 | 11-15 | 5 | 5-6 | 5 | 4-6 | 5-6 | 4
E | >7 | >8 | >6 | >5 | >15 | >5 | >6 | >5 | >6 | >6 | >4
| B | A | A | A | A | A | C | B | A | A | A | Análise ao Óleo TP 400 kV - SE3 - TP4 | 2002
Number | 3 | 4 | 4 | 4 | 4 | 4 | 2 | 3 | 4 | 4 | 4 | Fixação dos transformadores anti-sísmico
Análise ao Óleo TP 400 kV - SE3-TP4
SE3-Substituição de silica no TP4 400/60
| Bushings | Oil leaks | Oil level | Infra-red | Cooling | Main Tank | Oil tank | Foundation | Grounding | Gaskets | Connectors | Conservação de Ruptores
2016 | B | A | A | A | A | A | C | B | A | A | A | Análise ao Óleo TP 400 kV - SE3-TP4 | 2003
2015 | B | A | A | A | A | A | C | B | A | A | A | SE3 - Análise ao Óleo TP 400 kV - TP4
2014 | B | A | A | A | A | A | C | B | A | A | A | SE3 - Análise ao Óleo TP 400 kV - TP4 | 2004
2013 | B | A | A | A | A | A | C | B | A | A | A | SE3 - Análise ao Óleo TP 400 kV - TP4
2012 | B | A | A | A | A | A | C | B | A | A | A | SE3: avaria ventilador do TP4 400/60,
2011 | B | A | A | A | A | A | C | B | A | A | A | SE3: avaria num ventilador do TP4 | 2005
2010 | B | A | A | A | A | A | B | B | A | A | A | SE3 - Análise ao Óleo TP 400 kV - TP4 | 2006
2009 | B | A | A | A | A | A | B | B | A | A | A | SE3 - Conservação de ruptor TP4 | 2005
2008 | B | A | A | A | A | A | B | B | A | A | A | SE3 - Análise ao Óleo TP 400 kV - TP4
2007 | A | A | A | A | A | A | B | B | A | A | A | SE3 - TP4 Substituição da Sílica Gel | 2006
2006 | A | A | A | A | A | A | B | B | A | A | A | SE3 - Análise ao Óleo TP 400 kV - TP4
2005 | A | A | A | A | A | A | B | B | A | A | A | SE3 - Análise ao Óleo TP 400 kV - TP4
2004 | A | A | A | A | A | A | B | B | A | A | A | SE3 - Análise ao Óleo TP 400 kV - TP4 | 2007
2003 | A | A | A | A | A | A | B | B | A | A | A | SE3 - Análise ao Óleo TP 400 kV - TP4
2002 | A | A | A | A | A | A | B | B | A | A | A | SE3:PQ no ligador travessia TP4 60 F0 | 2008
SE3- Análise ao Óleo TR 400 kV - TP4
SE3- Análise ao Óleo TR 400 kV - TP4
SE3 - Análise ao Óleo TP 400 kV - TP4
SE3 - Análise ao Óleo TP 400 kV - TP4
SE3 - Análise ao Óleo TP 400 kV - TP4
[12 empty] | SE3 - TP4 Fuga de óleo | 2009
SE3 - Análise ao óleo TP4
[12 empty] | SE3 - Substituição de silica no TP4 | 2011
[12 empty] | SE3-Ensaios no TP4 400/60KV | 2012
[12 empty] | SE3 - TP4 Substituição da Sílica gel | 2013
SE3-Reparação de fugas
[12 empty] | SE3-avaria termostato arranque vent TP4 | 2012
[12 empty] | SE3-Análise ao óleo TP4 | 2014
[12 empty] | SE3-Ensaios ao óleo isolante TP4 | 2015
[12 empty] | SE3-Análise ao óleo TP4 | 2017

## Overall Condition
Overall Condition
Rating Code | Criterion 1 | Criterion 2 | Number
A | <3 WOs last 2 years | <10% increase last 5 years | 4
B | >3 WOs last 2 years AND >10% increase last 5 years | >5 WOs last 2 years | 3
C | >5 WOs last 2 years AND >30% increase last 5 years | >10 WOs last 2 years | 2
D | >10 WOs last 2 years AND >50% increase last 5 years | >15 WOs last 2 years | 1
E | >15 WOs last 2 years AND >80% increase last 5 years | >20 WOs last 2 years | 0
Number | Rating Code | Date |  | Análise ao Óleo TP 400 kV - SE3 - TP4 | 2002-10-01 | 2002-10-01 | 2002
3 | B | 2002 |  | Fixação dos transformadores anti-sísmico | 2002-04-02 | 2002-04-03
3 | B | 2003 |  | Análise ao Óleo TP 400 kV - SE3-TP4 | 2002-05-31 | 2002-05-31
3 | B | 2004 |  | SE3-Substituição de silica no TP4 400/60 | 2002-06-13 | 2002-06-13
4 | A | 2005 |  | Conservação de Ruptores | 2002-07-01 | 2002-07-01
4 | A | 2006 |  | Análise ao Óleo TP 400 kV - SE3-TP4 | 2003-01-02 | 2003-01-02 | 2003
4 | A | 2007 |  | SE3 - Análise ao Óleo TP 400 kV - TP4 | 2003-07-17 | 2003-07-17
3 | B | 2008 |  | SE3 - Análise ao Óleo TP 400 kV - TP4 | 2004-02-05 | 2004-02-05 | 2004
3 | B | 2009 |  | SE3 - Análise ao Óleo TP 400 kV - TP4 | 2004-08-26 | 2004-08-26
4 | A | 2010 |  | SE3: avaria ventilador do TP4 400/60, | 2004-08-02 | 2004-08-04
4 | A | 2011 |  | SE3: avaria num ventilador do TP4 | 2005-01-14 | 2005-01-14 | 2005
4 | A | 2012 |  | SE3 - Análise ao Óleo TP 400 kV - TP4 | 2006-08-30 | 2006-08-30 | 2006
4 | A | 2013 |  | SE3 - Conservação de ruptor TP4 | 2005-06-25 | 2005-06-27 | 2005
4 | A | 2014 |  | SE3 - Análise ao Óleo TP 400 kV - TP4 | 2005-07-13 | 2005-07-13
4 | A | 2015 |  | SE3 - TP4 Substituição da Sílica Gel | 2006-11-21 | 2006-11-21 | 2006
4 | A | 2016 |  | SE3 - Análise ao Óleo TP 400 kV - TP4 | 2006-01-31 | 2006-01-31
4 | A | 2017 |  | SE3 - Análise ao Óleo TP 400 kV - TP4 | 2006-08-01 | 2006-08-01
|  |  |  | SE3 - Análise ao Óleo TP 400 kV - TP4 | 2007-03-05 | 2007-03-05 | 2007
|  |  |  | SE3 - Análise ao Óleo TP 400 kV - TP4 | 2007-04-19 | 2007-04-19
|  |  |  | SE3:PQ no ligador travessia TP4 60 F0 | 2008-01-04 | 2008-01-04 | 2008
|  |  |  | SE3- Análise ao Óleo TR 400 kV - TP4 | 2008-05-13 | 2008-05-13
|  |  |  | SE3- Análise ao Óleo TR 400 kV - TP4 | 2008-05-13 | 2008-05-13
|  |  |  | SE3 - Análise ao Óleo TP 400 kV - TP4 | 2008-09-29 | 2008-09-29
|  |  |  | SE3 - Análise ao Óleo TP 400 kV - TP4 | 2008-09-29 | 2008-09-29
|  |  |  | SE3 - Análise ao Óleo TP 400 kV - TP4 | 2008-08-01 | 2008-08-01
|  |  |  | SE3 - TP4 Fuga de óleo | 2009-04-16 | 2009-04-16 | 2009
|  |  |  | SE3 - Análise ao óleo TP4 | 2009-07-22 | 2009-07-22
|  |  |  | SE3 - Substituição de silica no TP4 | 2011-12-28 | 2011-12-28 | 2011
|  |  |  | SE3-Ensaios no TP4 400/60KV | 2012-12-19 | 2012-12-19 | 2012
|  |  |  | SE3 - TP4 Substituição da Sílica gel | 2013-06-27 | 2013-06-27 | 2013
|  |  |  | SE3-Reparação de fugas | 2013-12-18 | 2013-12-18
|  |  |  | SE3-avaria termostato arranque vent TP4 | 2012-11-19 | 2012-11-19 | 2012
|  |  |  | SE3-Análise ao óleo TP4 | 2014-01-09 | 2014-01-09 | 2014
|  |  |  | SE3-Ensaios ao óleo isolante TP4 | 2015-07-21 | 2015-07-21 | 2015
|  |  |  | SE3-Análise ao óleo TP4 | 2017-01-27 | 2017-01-27 | 2017

## Final Calculation
HI Calculation
[8 empty] | 2016 | 83 | HI | DGA e OQF não têm 2016 | 1997-01-02 | 4 | 1997-05-19 | 1 | 1996-07-01 | 4 | 1993-10-25 | 4
| HIF |  |  | Date |  |  |  | 2015 | 83 |  |  | 1997-06-25 | 4 |  |  | 1997-01-02 | 4 | 1996-07-01 | 4
DGAF | 4 | 40 | 40 | 2015-09-03 09:00 |  |  |  | 2014 | 83 |  |  | 1997-12-22 | 4 | PF | 1 | 1997-06-25 | 4 | 1997-01-02 | 4
Load History | 4 | 40 | 40 |  |  |  |  | 2013 | 83 | ano em falta usei do ano anterior |  | 1999-02-11 | 4 |  |  | 1997-12-22 | 4 | 1997-06-25 | 4
Power Factor | 1 | 10 | 40 | 1997-05-19 |  |  |  | 2012 | 83 |  |  | 1999-07-23 | 4 | 2002 | 3 | 1999-02-11 | 3 | 1997-12-22 | 4
Infra-Red | 4 | 40 | 40 |  |  |  |  | 2011 | 80 | ano em falta usei do ano anterior |  | 2000-02-11 | 4 | 2003 | 3 | 1999-07-23 | 3 | 1999-02-11 | 4
OQF | 2 | 12 | 24 | 2015-09-03 09:00 |  |  |  | 2010 | 83 | 2-fal não tem a partir daqui |  | 2000-10-09 | 4 | 2004 | 3 | 2000-02-11 | 4 | 1999-07-23 | 4
Overall Condition | 4 | 32 | 32 | 2011 |  |  |  | 2009 | 80 |  |  | 2001-02-16 | 4 | 2005 | 4 | 2000-10-09 | 4 | 2000-02-11 | 4
2-FAL | 4 | 20 | 20 | 2010-07-08 | HI |  | Condition | 2008 | 80 |  |  | 2001-08-07 | 4 | 2006 | 4 | 2001-02-16 | 3 | 2000-10-09 | 4
Bushings | 3 | 15 | 20 |  | 0.83333 | 83.3333 | Good | 2007 | 84 |  |  | 2002-01-18 | 4 | 2007 | 4 | 2001-08-07 | 3 | 2001-02-16 | 4
Oil leaks | 4 | 4 | 4 |  |  |  |  | 2006 | 84 |  |  | 2003-01-15 | 4 | 2008 | 3 | 2002-01-18 | 3 | 2001-08-07 | 4
Oil level | 4 | 4 | 4 |  | HI | Condition | Approximate Expected Lifetime | 2005 | 87 |  |  | 2004-02-05 | 4 | 2009 | 3 | 2003-01-15 | 3 | 2002-01-18 | 4
Cooling | 4 | 8 | 8 |  | 85-100 | Very Good | More than 15 years | 2004 | 85 |  |  | 2005-02-10 | 4 | 2010 | 4 | 2003-07-17 | 3 | 2002-08-12 | 4
Main Tank | 4 | 8 | 8 |  | 70-85 | Good | More than 10 years | 2003 | 85 |  |  | 2006-01-31 | 4 | 2011 | 4 | 2004-02-05 | 3 | 2003-01-15 | 4
Oil tank | 2 | 2 | 4 |  | 50-70 | Fair | From 3 to 10 years | 2002 | 85 |  |  | 2007-04-19 | 4 | 2012 | 4 | 2004-08-26 | 3 | 2003-07-17 | 4
Foundation | 3 | 3 | 4 |  | 30-50 | Poor | Less than 3 years |  |  |  |  | 2008-03-14 | 4 | 2013 | 4 | 2005-02-10 | 3 | 2004-02-05 | 4
Grounding | 4 | 4 | 4 |  | 0-30 | Very Poor | At End of life |  |  |  |  | 2009-02-25 | 4 | 2014 | 4 | 2005-07-13 | 3 | 2004-08-26 | 4
Gaskets | 4 | 4 | 4 | [8 empty] | 2010-07-08 | 4 | 2015 | 4 | 2006-01-31 | 3 | 2005-02-10 | 4
Connectors | 4 | 4 | 4 | [10 empty] | 2016 | 4 | 2006-11-30 | 3 | 2005-07-13 | 4
[14 empty] | 2017 | 4 | 2007-04-19 | 3 | 2006-01-31 | 3
[16 empty] | 2007-11-08 | 3 | 2006-11-30 | 3
[12 empty] | 2-FAL | 4 | Overall | 4 | 2008-03-14 | 3 | 2007-04-19 | 3
[16 empty] | 2008-09-04 | 3 | 2007-11-08 | 3
[16 empty] | 2009-02-25 | 3 | 2008-03-14 | 3
[16 empty] | 2009-10-09 | 3 | 2008-09-04 | 3
[16 empty] | 2010-07-08 | 2 | 2009-02-25 | 3
[16 empty] | 2010-12-02 | 2 | 2009-10-09 | 3
[16 empty] | 2012-06-26 | 2 | 2010-07-08 | 4
[16 empty] | 2014-01-14 | 2 | 2010-12-02 | 3
[16 empty] | 2015-09-03 09:00 | 2 | 2012-06-26 | 4
[18 empty] | 2014-01-14 | 4
[16 empty] | OQF | 2 | 2015-09-03 09:00 | 4
[18 empty] | DGAF | 4